SPECIFICATIONS                                                                                                                                Domestic Pump B Pump and Motor

SPECIFICATIONS                                                                                                                                Domestic Pump B Pump and Motor

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

Division 23 – Heating, Ventilating and Air Conditioning (HVAC)

Section 23 20 00

HVAC Piping and Pumps

PART 1 GENERAL

1.01       SECTION INCLUDES

# Unit shall be a Domestic series B35, HB35, or HB17,

# 2 Ft. NPSH centrifugal pump as manufactured by Bell & Gossett, a Xylem brand.

# Furnish and install an extended life pump with a capacity as indicated in the plans.

1.02       RELATED SECTIONS

- Section 23 22 23 – Steam Condensate Pumps

- Section 23 22 23.13 -  Electric Driven Condensate Pumps

- Section 23 22 23.23  – Pressure Powered Steam Condensate Pumps

1.03       REFERENCES

- HI - Hydraulic Institute.

- ANSI - American National Standards Institute.

- NEMA - National Electrical Manufacturers Association.

- UL - Underwriters Laboratories.

- ETL - Electrical Testing Laboratories.

- CSA - Canadian Standards Association.

- NEC - National Electric Codes.

- ISO - International Standards Organization.

- IEC - International Electrotechnical Commission.

1.04       SUBMITTALS

- Submit data cover sheet.

- Unit description sheet.

- Dimensional print(s).

- Sales bulletin.

- Piping diagram(s).

- Wiring diagram(s).

- Installation, operation & maintenance manual.

1.05      QUALITY ASSURANCE

- The manufacturer shall have a minimum of 30 years experience in the design and construction of condensate return equipment.

- The pump manufacturer shall be fully certified by the International Standards Organization per ISO 9001. Proof of this certification shall be furnished at the time of submittal.

# The manufacturer shall carry a minimum product liability insurance of $5,000,000.00 per occurrence.

# The pump manufacturer shall test according to the ANSI/Hydraulics

# Institute Standard 14.6, Grade 1, for Rate of Flow, Total Head and

# Power Consumption.

PART 2 PRODUCTS

2.01      MANUFACTURERS

# Subject to compliance with these specifications, the following manufacturers shall be acceptable:

- Bell & Gossett, a Xylem brand Domestic series B35, HB35 or HB17.

- Pre-approved equal.

2.02       COMPONENTS

# Water pump

# 1. The water pump shall be two-staged, centrifugal design, bronze fitted with enclosed cast bronze centrifugal impeller, permanently aligned and flanged mounted for vertical operation.

# 2. Capacities and electrical characteristics for the pump shall be scheduled on the drawings.

# 3. Each pump gpm shall be sized for 2 times the system return rate.

# 4. Each pump shall deliver its full capacity with condensate temperatures up to 210°F (99°C) at sea level, at 2 ft. NPSH (net positive suction head) or with condensate temperatures up to 212°F (100°C) at sea level, at 2 ft. NPSH (net positive suction head) when the water column is elevated continously 2 ft above the suction of the pump.

# 5. Carbon/ceramic mechanical shaft seal shall be rated for 250°F (121°C).

# 6. Each pump shall include:

# Axial flow, first-stage impeller

# Dynamically balanced, cast bronze impeller

# Bronze straightening vanes

# Renewable bronze casing wear ring

# Stainless steel shaft

# Discharge gauge port tapping

# Drain tapping

# 7. The water pump shall be constructed of one of the following:

# Series HB35 or HB17 bronze fitted, centrifugal design pump, close-coupled to a 3500 RPM motor or 1750 RPM motor, respectively, permanently aligned, and flange mounted for horizontal operation.

# Series B35 bronze fitted, centrifugal design pump, close-coupled to a 3500 RPM motor, respectively, permanently aligned, and flange mounted for vertical operation.

# Series HB35 or HB17 bronze fitted, centrifugal design pump, close-coupled to a 3500 RPM motor or 1750 RPM motor, respectively, permanently aligned, and flange mounted for horizontal operation.

# 8. The pump shall include:

# a.One dynamically balanced enclosed bronze centrifugal impeller for  Series HB35, HB17 or B35.

# b. One renewable bronze wearing ring for Series HB35, HB17 or B35.

# One stainless steel shaft.

# 9. The motor shall meet NEMA specifications and shall be the size, voltage, insulation class, duty rating and enclosure called for in the plans.

- Optional TEFC motor as required.

PART 3 EXECUTION

  - INSTALLATION

- Install equipment in accordance with manufacturer’s instructions.

- Power wiring, as required, shall be the responsibility of the electrical contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal and local codes.

- All factory wiring shall be numbered or coded for easy identification and the numbers shall coincide with those shown on the wiring diagram.

- The unit shall be factory tested as a complete unit and the unit manufacturer shall furnish elementary and connection-wiring diagrams and piping diagrams. Installation and operation instructions shall also be provided.

- The unit shall be shipped completely assembled.

- The factory shall provide a certified test report.

- Unit shall be a Domestic series B35, HB35, HB17, as manufactured by Bell & Gossett, a Xylem brand, Morton Grove, IL.

###### END OF SECTION

www.bellgossett.com

Bell & Gossett is a trademark of Xylem Inc. or one of its subsidiaries.

© 2018 Xylem Inc.  Domestic Pump B Pump and Motor Specifications