SPECIFICATIONS                                                                                                                                Triple Duty Valve – Angle Pattern

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

# SECTION 23 05 93

Testing, Adjusting, and Balancing for HVAC

PART 1 GENERAL

1.01       SECTION INCLUDES

# Unit shall be a Bell & Gossett Triple Duty Valve, as manufactured by Xylem.

# Furnish Triple Duty Valve with capabilities as indicated in the plans.

1.02       RELATED SECTIONS

- Section 23 01 70 – Operation & Maintenance of Central HVAC Equipment

- Section 23 08 00 – Commissioning of HVAC

- Section 23 05 23 – General Duty Valves for HVAC Piping

- Section 23 20 00 – HVAC Piping and Pumps

- Section 23 21 13 – Hydronic Piping

- Section 23 21 16 – Hydronic Piping Specialties

- Section 23 21 23 – Hydronic Pumps

- Section 23 21 23.13 – In-Line Centrifugal Hydronic Pumps

- Section 23 21 23.16 – Base-Mounted, Centrifugal Hydronic Pumps

- Section 23 21 23.19 – Vertical-Mounted, Double-Suction Centrifugal Hydronic Pumps

1.03       REFERENCES

- ANSI – American National Standards Institute..

- ISO – International Standards Organization.

1.04       SUBMITTALS

- Submit data cover sheet.

- Dimensional print(s).

- Sales bulletin.

- Installation, operation & maintenance manual.

1.05      QUALITY ASSURANCE

- The product manufacturer shall be fully certified by the International Standards Organization 
per ISO 9001.

# The manufacturer shall carry a minimum product liability insurance of $5,000,000.00 per occurrence.

1.06      MAINTENANCE MATERIAL SUBMITTALS

PART 2 PRODUCTS

2.01      MANUFACTURERS

# Subject to compliance with these specifications, the following manufacturers shall be acceptable:

- Triple Duty Valve

- Xylem Inc. Bell & Gossett Model 3D-__S.

- Pre-approved equal.

2.02      COMPONENTS

- Triple Duty Valve

- The valve shall be an angle pattern, non-adjustable design.

- The valve shall be a globe valve design.

- The valve shall have a spring-loaded check valve design to prevent gravity circulation and backflow.

- The valve shall have a calibrated nameplate with multi-turn stem.

- The valve shall include a rubber memory button to allow the valve to be re-balanced to its original position after shut-off or maintenance.

- The valve shall have a fully backseating disc to allow the valve packing to be replaced while under pressure.

- The valve body shall be made of either cast iron or ductile iron.

- The valve disc shall be made of brass with an EPDM rubber seat.

- The valve stem shall be made of stainless steel.

- The valve spring shall be made of stainless steel.

- The valve shall have flanged end connections.

- Flange end connections should be designed according to ANSI Class 150 Standards.

- The valve shall be rated for 175 psi (1,207 kPa) maximum working pressure.

- The valve shall have a maximum temperature rating of 250°F (121°C).

2.03      ACCESSORIES

- Triple Duty Valve Accessories

- Pressure/Temperature port.

PART 3 EXECUTION

  - INSTALLATION

- Install Triple Duty Valve in accordance with manufacturer’s instructions.

- Unit shall be a Bell & Gossett Triple Duty Valve Model 3D-__S as manufactured by Xylem.

###### END OF SECTION

www.bellgossett.com

Bell & Gossett is a trademark of Xylem Inc. or one of its subsidiaries.

© 2016 Xylem Inc.   Triple Duty Valve – Angle Pattern August 2016