Tender Number / Project name: XXXXXXX

Date: XX. XX. XXXX

TECHNICAL PROCUREMENT SPECIFICATION

| Item. | Qty. | Technical description | Price per unit | Amount |
| --- | --- | --- | --- | --- |
|  |  | Agitator for aeration tank Task The solids (mud flakes, mud, fibers, Sands, etc.) in the treated wastewater must be kept in suspension and the velocity of the liquid in the complete basin shall have a velocity between 0,20 - 0,30 m/s to avoid the sedimentation of solids. Technical details of the basins Activated sludge: 2 - 6 g/l dry solids Sludge Volume Index (SVI) 50 - 150 ml/g Number of basins: X Basin shape: XXXXXXXXXXXXXXX Dimensions: diameter X m / length X m / channel width X m Water depth = XX m Volume per basin: approx. XXXX m3 Number of agitators: X unit per basin Propeller diameter: 2.5 m Range of thrust: at least XXXX to XXXX N (F) To minimize the power consumption it shall be possible to adjust the required propeller speed and trust during the Nitrification and Denitrification phase. The agitator shall be equipped with an internal frequency drive (VFD) and a RS485 + Modbus RTU interface that can be controlled via a PLC. The use of an external VFD to modify the propeller speed is accepted if the cost is included in the price of the Agitator. The supplier must guarantee the following performance. Required performance and max. Power consumption during Nitrification (Aeration on): Propeller speed: XX min-1 Guaranteed thrust: XXXX N Max. Power consumption: XX kW (P1) Specif. Thrust vs. power: XXX N / kW (F / P1) according to ISO 21630 Specif. Energy consumption per m3: XX W / m3 (P1 total / V) Required performance and max. Power consumption during Denitrification (Aeration off): Propeller speed: XX min-1 Guaranteed thrust: XXXX N Max. Power consumption: XX kW (P1) Specif. Thrust vs. power: XXX N / kW (F / P1) according to ISO 21630 Specif. Energy consumption per m3: XX W / m3 (P1 total / V) |  |  |
| 1.01 |  | Submersible Agitator The Agitator shall be capable of handling raw, screened sewage. It shall be possible to easily raise and lower the mixer on a 100x100 mm guide bar system without the need for personnel to enter the tank. The agitator, the motor and the cable, shall be capable of continuous submergence without loss of watertight integrity to a depth of 20 m according IP 68. Rated Power P2: >= XX kW Motor efficiency class. IE4 It shall be possible to run the motor on 380-480V at 50 or 60Hz. Starting method: Speed ramp up at reduced current. Motor and drive The mixer shall have a high efficiency synchronous speed motor with an integrated variable speed drive, housed in an air filled, watertight chamber. The motor efficiency shall be equivalent to IE4 levels. The shaft speed shall be adjustable via a gateway with Modbus RTU / TCP 4-2m0 mA signals. The drive shall monitor temperature and current and stop the mixer in case of overload. The Stator shall be inverter duty rated in accordance with NEMA MG1, Part 31 and be insulated according class H 180°C (356°F). The motor shall be capable of an unlimited number starts per hour. The motor shall be equipped with 10m submersible and screened cable including 2 leads for the sensors. The cable entry seal shall consist of cylindrical elastomer bushings, without epoxies, silicones or other secondary sealing systems. Gear unit The gearbox shall be of a two-stage helical type equipped with high precision, low loaded gears. The motor shaft shall be provided with an integral driving gear. The intermediate shaft shall rotate in two spherical roller bearings and contain a second driving gear. The propeller shaft shall contain the second driven gear and rotate in one single row and one double row angular contact ball bearing or roller bearing. Material and Coating Major components excluding stand and propeller blades shall be of grey cast iron EN1561-GJL250. The total layer thickness should be at least 350 microns. All cast iron surfaces in contact with the mixed liquid shall be protected by a factory applied spray topcoat of oxiranesther (Duasolid 50). Fasteners shall be made of stainless steel AISI 316. The propeller shaft shall be made of stainless steel 1.4057, or comparable. Propeller The propeller shall consist of fibreglass reinforced polyurethane blades each integrated with stainless steel shaft for mounting in a cast iron hub. The propeller blade shape shall be a clogging-resistant, backswept design. Propeller diameter shall be: 2500 mm Bearings The motor shaft shall rotate on two permanently lubricated bearings. The inner bearing shall be single row deep grove ball bearing and the main bearing a spherical roller bearing. Mechanical seals Each Agitator shall have an oil chamber for the shaft sealing system, and a second separate oil chamber for the gearbox. Plugs for drainage and inspection of the oil shall be easily accessible from the outside. Each agitator shall have with three seals to separate the various parts of the mixer. The outer seal on the propeller shaft shall be a mechanical seal made of corrosion resistant cemented carbide (WCCR). The seals shall operate in an oil reservoir that hydro dynamically lubricates the seal faces at a constant rate. The seals shall require neither maintenance nor adjustment. OIL The oil chamber shall be filled with a medical white oil. This oil must be approved according to FDA 172.878. The gearbox chamber shall be filled with a gearbox oil of type Mobil gear 630 or similar. The Agitator shall be equipped with an extended lifting handle. Factory testing The manufacturer shall have the capability of acceptance testing the mixer regarding thrust and power according to ISO 21630:2007, on request. The supplier shall present an assembly control plan according to ISO 9001, which confirms the execution of the following tests. 1. Tightness test of the assembled mixer using a vacuum method. 2. Dry-run test to establish mechanical integrity and correct rotation. Model: FLYGT SR 4320 or equivalent | X,- | X,- |
| 1.02 |  | Installation set for permanent installation of Submersible agitator. The installation set shall contain: 1 freestanding tripod guide bar 100x100x 4mm for floor mounting including anchor bolts. The guide bar shall be applicable for an installation depth up to 6 m The guide bar shall have a support for the agitator. During operation, the wire shall not suspend the agitator. The guide bar and anchor bolts shall be made of AISI 316 (1.4571) The supplier of the agitator shall provide an installation drawing with detailed instruction about the position and orientation of the Agitator. | X,- | X,- |
| 1.02A |  | Installation set for permanent installation of Submersible agitator. The installation set shall contain: 1 freestanding tripod guide bar 100x100x 4mm for floor mounting including anchor bolts. The guide bar shall be applicable for an installation depth up to 6 m The guide bar shall have a support for the agitator. During operation, the wire shall not suspend the agitator. The guide bar and anchor bolts shall be made of AISI 304 The supplier of the agitator shall provide an installation drawing with detailed instruction about the position and orientation of the Agitator. | X,- | X,- |
| 1.03. |  | Mobile Lifting davit for Agitator or pump Adjustable for reach and height, Reach 650 - 1200 mm, Including Winch with bracket and 15-meter wire. Max. lifting load: 320 kg Material: David: Stainless steel EN 1.4301 or AISI 304 Winch: Stainless steel or Aluminium Hook & Lifting wire: Stainless steel AISI 316 Model: FLYGT SK 320 or equivalent | X,- | X,- |
| 1.03A |  | Mobile Lifting davit for Agitator or pump Adjustable for reach and height, Reach 1600 - 2000 mm, Including Winch with bracket and 15-meter wire. Max. lifting load: 300 kg Material: David: Stainless steel EN 1.4301 or AISI 304 Winch: Stainless steel or Aluminium Hook & Lifting wire: Stainless steel AISI 316 Model: FLYGT SK 300 or equivalent | X,- | X,- |
| 1.04 |  | Lifting device with automatic hook Shall enable the operator to catch, lift, lower and release the Agitator below water level. Material: Stainless steel 1.4436 Model: FLYGT AVR 834126 or equivalent | X,- | X,- |
| 1.05 |  | Floor mounted David holder including anchor bolts Material: Stainless steel AISI 316 | X,- | X,- |
| 1.05A |  | Option: Wall mounted David holder including anchor bolts. Material: Stainless steel AISI 316 | X,- | X,- |
| 2.01 |  | PLC control Cabinet for Agitator The cabinet shall be made of Reinforced plastic or stainless steel and it shall be prepared for an installation on a wall and be isolated according protection class IP 66. It shall contain following equipment: 1 Power switch, which can be locked in the off position 1 Communication gateway Modbus RTU/TCP 4-20mA 1 A Job wheel operator panel 1 Heating element with thermostat Power supply shall ne 24 V DC Model: FLYGT VOS-Standard III (FOP315+APP412) or equivalent | X,- | X,- |
| 3.01 |  | Delivery of described agitator and accessories according incoterm DAP to XXXXXXXXXXXXXXX |  | X,- |
| 3.02 |  | Installation of described Agitator and accessories Under the condition that that the Basins are accessible with a truck and that lifting gear is available. Place of Installation: XXXXXXXXXXXXXXXXX |  | X,- |