## rivo_modbus
Modbus Reference List
Rivo I - III | [5 empty] | Ver.: V2.1.1
2026-05-21
Modbus Register | Bit | Type | No. of bytes | Access | Designation | Description
Process values | [5 empty] | Only the registers for which there is a measurement or a controller are available. The value "0" is returned in the remaining registers.
0 |  | FLOAT | 4 | R | Temperature
2 |  | ASCII | 8 | R | Temperature Unit | e.g. "°C"
6 |  | UINT16 | 2 | R | Temperature error status | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error
| 11 |  |  |  | Hardware error 4 | Factory calibration missing.
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
7 |  | FLOAT | 4 | R | Flow
9 |  | ASCII | 8 | R | Flow Unit | e.g. "%"
13 |  | UINT16 | 2 | R | Flow error status | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error
| 11 |  |  |  | Hardware error 4 | Factory calibration missing.
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
14 |  | FLOAT | 4 | R | Measurement 1 Measured value
16 |  | ASCII | 8 | R | Measurement 1 Unit | e.g. "mg/l"
20 |  | UINT16 | 2 | R | Measurement 1 error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
21 |  | FLOAT | 4 | R | Measurement 2 Measured value
23 |  | ASCII | 8 | R | Measurement 2 Unit | e.g. "mg/l"
27 |  | UINT16 | 2 | R | Measurement 2 error staus | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
28 |  | FLOAT | 4 | R | Measurement 3 Measured value
30 |  | ASCII | 8 | R | Measurement 3 Unit | e.g. "mg/l"
34 |  | UINT16 | 2 | R | Measurement 3 error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
35 |  | FLOAT | 4 | R | Measurement 4 Measured value
37 |  | ASCII | 8 | R | Measurement 4 Unit | e.g. "mg/l"
41 |  | UINT16 | 2 | R | Measurement 4 error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
42 |  | FLOAT | 4 | R | Measurement 5 Measured value
44 |  | ASCII | 8 | R | Measurement 5 Unit | e.g. "mg/l"
48 |  | UINT16 | 2 | R | Measurement 5 error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
49 |  | FLOAT | 4 | R | Measurement 6 Measured value
51 |  | ASCII | 8 | R | Measurement 6 Unit | e.g. "mg/l"
55 |  | UINT16 | 2 | R | Measurement 6 error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
56 |  | INT32 | 4 | R | reserved
58 |  | INT32 | 4 | R | reserved
60 |  | FLOAT | 4 | R | Controller 1 Dosing output | [%]
62 |  | UINT16 | 2 | R | Controller 1 Status | 0 = Off 1 = On
63 |  | UINT16 | 2 | RW | Controller 1 Operation mode | 0 = Automatic 1 = Manual
64 |  | FLOAT | 4 | R | Controller 1 act. Setpoint | [user defined unit], only with Single feedback control and Compound loop
66 |  | FLOAT | 4 | R | Controller 1 act. Dosing factor | [%], only at Proportional control
68 |  | FLOAT | 4 | R | Controller 2 Dosing output | [%]
70 |  | UINT16 | 2 | R | Controller 2 Status | 0 = Off 1 = On
71 |  | UINT16 | 2 | RW | Controller 2 Operation mode | 0 = Automatic 1 = Manual
72 |  | FLOAT | 4 | R | Controller 2 act. Setpoint | [user defined unit], only with Single feedback control and Compound loop
74 |  | FLOAT | 4 | R | Controller 2 act. Dosing factor | [%], only at Proportional control
76 |  | FLOAT | 4 | R | Controller 3 Dosing output | [%]
78 |  | UINT16 | 2 | R | Controller 3 Status | 0 = Off 1 = On
79 |  | UINT16 | 2 | RW | Controller 3 Operation mode | 0 = Automatic 1 = Manual
80 |  | FLOAT | 4 | R | Controller 3 act. Setpoint | [user defined unit], only with Single feedback control and Compound loop
82 |  | FLOAT | 4 | R | Controller 3 act. Dosing factor | [%], only at Proportional control
84 |  | FLOAT | 4 | R | Controller 4 Dosing output | [%]
86 |  | UINT16 | 2 | R | Controller 4 Status | 0 = Off 1 = On
87 |  | UINT16 | 2 | RW | Controller 4 Operation mode | 0 = Automatic 1 = Manual
88 |  | FLOAT | 4 | R | Controller 4 act. Setpoint | [user defined unit], only with Single feedback control and Compound loop
90 |  | FLOAT | 4 | R | Controller 4 act. Dosing factor | [%], only at Proportional control
92 |  | FLOAT | 4 | R | Controller 5 Dosing output | [%]
94 |  | UINT16 | 2 | R | Controller 5 Status | 0 = Off 1 = On
95 |  | UINT16 | 2 | RW | Controller 5 Operation mode | 0 = Automatic 1 = Manual
96 |  | FLOAT | 4 | R | Controller 5 act. Setpoint | [user defined unit], only with Single feedback control and Compound loop
98 |  | FLOAT | 4 | R | Controller 5 act. Dosing factor | [%], only at Proportional control
Inputs and Outputs | [5 empty] | Only the registers for which there is a measurement or a controller are available. The value "0" is returned in the remaining registers
200 |  | FLOAT | 4 | R | Analog input 1 | [%]
202 |  | FLOAT | 4 | R | Analog input 2 | [%]
204 |  | FLOAT | 4 | R | reserved
206 |  | FLOAT | 4 | R | reserved
208 |  | FLOAT | 4 | R | reserved
210 |  | FLOAT | 4 | R | reserved
212 |  | FLOAT | 4 | R | reserved
214 |  | FLOAT | 4 | R | reserved
216 |  | FLOAT | 4 | R | reserved
218 |  | FLOAT | 4 | R | reserved
220 |  | FLOAT | 4 | R | reserved
222 |  | FLOAT | 4 | R | reserved
224 |  | FLOAT | 4 | R | reserved
226 |  | FLOAT | 4 | R | reserved
228 |  | FLOAT | 4 | R | reserved
230 |  | FLOAT | 4 | R | reserved
232 |  | FLOAT | 4 | R | Analog output 1 | [%]
234 |  | FLOAT | 4 | R | Analog output 2 | [%]
236 |  | FLOAT | 4 | R | Analog output 3 | [%]
238 |  | FLOAT | 4 | R | Analog output 4 | [%]
240 |  | FLOAT | 4 | R | Analog output 5 | [%]
242 |  | FLOAT | 4 | R | Analog output 6 | [%]
244 |  | FLOAT | 4 | R | Analog output 7 | [%]
246 |  | FLOAT | 4 | R | Analog output 8 | [%]
248 |  | FLOAT | 4 | R | reserved
250 |  | FLOAT | 4 | R | reserved
252 |  | FLOAT | 4 | R | reserved
254 |  | FLOAT | 4 | R | reserved
256 |  | FLOAT | 4 | R | reserved
258 |  | FLOAT | 4 | R | reserved
260 |  | FLOAT | 4 | R | reserved
262 |  | FLOAT | 4 | R | reserved
264 |  | UINT16 | 2 | R | Digital inputs with direction function | 1 = Active Status with set direction (inverse, direct)
| 0 |  |  |  | DI 1
| 1 |  |  |  | DI 2
| 2 |  |  |  | DI 3
| 3 |  |  |  | DI 4
| 4 |  |  |  | DI 5
| 5 |  |  |  | DI 6
| 6 |  |  |  | DI 7
| 7 |  |  |  | DI 8
| 8 |  |  |  | DI 9
| 9 |  |  |  | DI 10
| 10 |  |  |  | DI 11
| 11 |  |  |  | DI 12
| 12 |  |  |  | DI 13
| 13 |  |  |  | DI 14
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
265 |  | UINT16 | 2 | R | Digital inputs | 1 = Active (contact closed) 0 = Inactive (contact open)
| 0 |  |  |  | DI 1
| 1 |  |  |  | DI 2
| 2 |  |  |  | DI 3
| 3 |  |  |  | DI 4
| 4 |  |  |  | DI 5
| 5 |  |  |  | DI 6
| 6 |  |  |  | DI 7
| 7 |  |  |  | DI 8
| 8 |  |  |  | DI 9
| 9 |  |  |  | DI 10
| 10 |  |  |  | DI 11
| 11 |  |  |  | DI 12
| 12 |  |  |  | DI 13
| 13 |  |  |  | DI 14
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
266 |  | UINT16 | 2 | R | Alarm relay/digital outputs | Status if direction is "Direct": 1 = Active, on 0 = Inactive, off Status if direction is "Inverse:": 1 = Inactive, off 0 = Active, on
| 0 |  |  |  | DO 1
| 1 |  |  |  | DO 2
| 2 |  |  |  | DO 3
| 3 |  |  |  | DO 4
| 4 |  |  |  | DO 5
| 5 |  |  |  | DO 6
| 6 |  |  |  | DO 7
| 7 |  |  |  | DO 8
| 8 |  |  |  | DO 9
| 9 |  |  |  | DO 10
| 10 |  |  |  | DO 11
| 11 |  |  |  | DO 12
| 12 |  |  |  | DO 13
| 13 |  |  |  | DO 14
| 14 |  |  |  | DO 15
| 15 |  |  |  | DO 16
267 |  | UINT16 | 2 | R | Relay/digital outputs | 1 = Active / switching status = On 0 = Inactive / switching status = Off
| 0 |  |  |  | DO 1
| 1 |  |  |  | DO 2
| 2 |  |  |  | DO 3
| 3 |  |  |  | DO 4
| 4 |  |  |  | DO 5
| 5 |  |  |  | DO 6
| 6 |  |  |  | DO 7
| 7 |  |  |  | DO 8
| 8 |  |  |  | DO 9
| 9 |  |  |  | DO 10
| 10 |  |  |  | DO 11
| 11 |  |  |  | DO 12
| 12 |  |  |  | DO 13
| 13 |  |  |  | DO 14
| 14 |  |  |  | DO 15
| 15 |  |  |  | DO 16
268 |  | UINT16 | 2 | R | Alarm relay/digital outputs | Status if direction is "Direct": 1 = Active, on 0 = Inactive, off Status if direction is "Inverse:": 1 = Inactive, off 0 = Active, on
| 0 |  |  |  | DO 17
| 1 |  |  |  | DO 18
| 2 |  |  |  | DO 19
| 3 |  |  |  | DO 20
| 4 |  |  |  | DO 21
| 5 |  |  |  | DO 22
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | reserved
| 9 |  |  |  | reserved
| 10 |  |  |  | reserved
| 11 |  |  |  | reserved
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
269 |  | UINT16 | 2 | R | Relay/digital outputs | 1 = Active / switching status = On 0 = Inactive / switching status = Off
| 0 |  |  |  | DO 17
| 1 |  |  |  | DO 18
| 2 |  |  |  | DO 19
| 3 |  |  |  | DO 20
| 4 |  |  |  | DO 21
| 5 |  |  |  | DO 22
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | reserved
| 9 |  |  |  | reserved
| 10 |  |  |  | reserved
| 11 |  |  |  | reserved
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
270 |  | INT16 | 2 | R | reserved
271 |  | INT32 | 4 | R | reserved
273 |  | INT32 | 4 | R | reserved
275 |  | UINT16 | 2 | R | Alarm configuration | 0 = Inactive 1 = Active
| 0 |  |  |  | Alarm 1
| 1 |  |  |  | Alarm 2
| 2 |  |  |  | Alarm 3
| 3 |  |  |  | Alarm 4
| 4 |  |  |  | Alarm 5
| 5 |  |  |  | Alarm 6
| 6 |  |  |  | Alarm 7
| 7 |  |  |  | Alarm 8
| 8 |  |  |  | reserved
| 9 |  |  |  | reserved
| 10 |  |  |  | reserved
| 11 |  |  |  | reserved
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
System messages | [5 empty] | The error codes are sorted according to the time stamp. The most recent message is error code 1. If there are more than 20 messages, the most recent 20 are displayed.
500 |  | UINT16 | 2 | R | Number of pending notifications
501 |  | UINT32 | 4 | RW | ACK | Set the corresponding error code to acknowledge. All messages are acknowledged with 0xFFFFFFFFFF.
503 |  | UINT32 | 4 | R | Error Code 1 | Code of the most recent message
505 |  | UINT32 | 4 | R | Time stamp 1 | Time at which the message occurred. Display as Unix time stamp
507 |  | UINT32 | 4 | R | Error Code 2
509 |  | UINT32 | 4 | R | Time stamp 2
511 |  | UINT32 | 4 | R | Error Code 3
513 |  | UINT32 | 4 | R | Time stamp 3
515 |  | UINT32 | 4 | R | Error Code 4
517 |  | UINT32 | 4 | R | Time stamp 4
519 |  | UINT32 | 4 | R | Error Code 5
521 |  | UINT32 | 4 | R | Time stamp 5
523 |  | UINT32 | 4 | R | Error Code 6
525 |  | UINT32 | 4 | R | Time stamp 6
527 |  | UINT32 | 4 | R | Error Code 7
529 |  | UINT32 | 4 | R | Time stamp 7
531 |  | UINT32 | 4 | R | Error Code 8
533 |  | UINT32 | 4 | R | Time stamp 8
535 |  | UINT32 | 4 | R | Error Code 9
537 |  | UINT32 | 4 | R | Time stamp 9
539 |  | UINT32 | 4 | R | Error Code 10
541 |  | UINT32 | 4 | R | Time stamp 10
543 |  | UINT32 | 4 | R | Error Code 11
545 |  | UINT32 | 4 | R | Time stamp 11
547 |  | UINT32 | 4 | R | Error Code 12
549 |  | UINT32 | 4 | R | Time stamp 12
551 |  | UINT32 | 4 | R | Error Code 13
553 |  | UINT32 | 4 | R | Time stamp 13
555 |  | UINT32 | 4 | R | Error Code 14
557 |  | UINT32 | 4 | R | Time stamp 14
559 |  | UINT32 | 4 | R | Error Code 15
561 |  | UINT32 | 4 | R | Time stamp 15
563 |  | UINT32 | 4 | R | Error Code 16
565 |  | UINT32 | 4 | R | Time stamp 16
567 |  | UINT32 | 4 | R | Error Code 17
569 |  | UINT32 | 4 | R | Time stamp 17
571 |  | UINT32 | 4 | R | Error Code 18
573 |  | UINT32 | 4 | R | Time stamp 18
575 |  | UINT32 | 4 | R | Error Code 19
577 |  | UINT32 | 4 | R | Time stamp 19
579 |  | UINT32 | 4 | R | Error Code 20
581 |  | UINT32 | 4 | R | Time stamp 20
External signals | [5 empty] | If the external signal (e.g. external flow or external measuremente value) is used as a signal source, the registers of the signals must be written cyclically. If it is not written again within the set time (timeout), it leads to a timeout and the corresponding controller switches off.
1000 |  | FLOAT | 4 | RW | External flow | [user defined unit]
1002 |  | FLOAT | 4 | RW | Start range | [user defined unit]
1004 |  | FLOAT | 4 | RW | End range | [user defined unit]
1006 |  | UINT16 | 2 | RW | reserved
1007 |  | ASCII | 8 | RW | Unit | If no unit is specified, the default unit is %. e.g. "m³/h"
1011 |  | FLOAT | 4 | RW | External measurement 1 | [user defined unit]
1013 |  | FLOAT | 4 | RW | Start range | [user defined unit]
1015 |  | FLOAT | 4 | RW | End range | [user defined unit]
1017 |  | UINT16 | 2 | RW | reserved
1018 |  | ASCII | 8 | RW | Unit | e.g. "mg/l"
1022 |  | FLOAT | 4 | RW | External measurement 2 | [user defined unit]
1024 |  | FLOAT | 4 | RW | Start range | [user defined unit]
1026 |  | FLOAT | 4 | RW | End range | [user defined unit]
1028 |  | UINT16 | 2 | RW | reserved
1029 |  | ASCII | 8 | RW | Unit | e.g. "pH"
System data
1500 |  | ASCII | 20 | RW | Device name | e.g. "rivo-system"
1510 |  | ASCII | 20 | RW | Application name | e.g. "Rivo"
1520 |  | ASCII | 20 | R | reserved
1530 |  | ASCII | 20 | R | Rivo OS Version | e.g. "1.0.2"
1540 |  | UINT16 | 2 | R | Year | e.g. 2024
1541 |  | UINT16 | 2 | R | Month | e.g. 4
1542 |  | UINT16 | 2 | R | Day | e.g. 21
1543 |  | UINT16 | 2 | R | Hour | e.g. 16
1544 |  | UINT16 | 2 | R | Minute | e.g. 45
1545 |  | ASCII | 16 | R | Serial number Device | e.g. "240300000019"
1553 |  | ASCII | 16 | R | Serial number HMI | e.g. "240300000019"
1561 |  | ASCII | 16 | RW | IP address | e.g. "192.168.100.31"
1569 |  | ASCII | 16 | RW | Subnetmask | e.g. "255.255.255.0"
1577 |  | ASCII | 16 | RW | Gateway | e.g. "0.0.0.0"
1585 |  | UINT16 | 2 | RW | DHCP | 0 = Off 1 = On
1586 |  | ASCII | 18 | R | MAC address | e.g. "fc:0f:e7:02:4b:8e"
1595 |  | UINT16 | 2 | R | Heartbeat | Increments by one every 500 ms. Heartbeat can be used to moni tor the up-to-dateness of the available data. The counter changes every 0.5 seconds.
1596 |  | ASCII | 20 | W | Modbus Password | e.g. "Password" Modbus password must be set before a write command if write protection is activated (= On with password). Writing values is possible for the period defined in the Password timeout menu. After expiry, the password must be set again before a write com mand.
Temperature | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2000 |  | FLOAT | 4 | R | Temperature
2002 |  | ASCII | 8 | R | Temperature Unit | e.g. "°C"
2006 |  | UINT16 | 2 | R | Temperature error status | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error
| 11 |  |  |  | Hardware error 4 | Factory calibration missing.
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2007 |  | FLOAT | 4 | R | Start range | [user defined unit]
2009 |  | FLOAT | 4 | R | End range | [user defined unit]
2011 |  | FLOAT | 4 | R | Range Base value | [°C]
2013 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2015 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. e.g. "mg/l"
2019 |  | FLOAT | 4 | R | Sensor signal
2021 |  | ASCII | 8 | R | Sensor signal unit | e.g. "°C"
2025 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2027 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2029 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2031 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2033 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2035 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2037 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2038 |  | ASCII | 20 | R | Label | e.g. "Temperature"
2048 |  | ASCII | 20 | R | Type of measurement | e.g. "Temperature"
Flow | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2100 |  | FLOAT | 4 | R | Flow
2102 |  | ASCII | 8 | R | Flow Unit | e.g. "%"
2106 |  | UINT16 | 2 | R | Flow error status | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error
| 11 |  |  |  | Hardware error 4 | Factory calibration missing.
| 12 |  |  |  | reserved
| 13 |  |  |  | reserved
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2107 |  | FLOAT | 4 | R | Start range | [user defined unit]
2109 |  | FLOAT | 4 | R | End range | [user defined unit]
2111 |  | FLOAT | 4 | R | Range Base value | [%]
2113 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2115 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. e.g. "mg/l"
2119 |  | FLOAT | 4 | R | Sensor signal
2121 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2125 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2127 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2129 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2131 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2133 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2135 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2137 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2138 |  | ASCII | 20 | R | Label | e.g. "Flow"
2148 |  | ASCII | 20 | R | Type of measurement | e.g. "Flow"
Measurement 1 | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2200 |  | FLOAT | 4 | R | Measurement
2202 |  | ASCII | 8 | R | Measurement Unit | e.g. "mg/l"
2206 |  | UINT16 | 2 | R | Measurement error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2207 |  | FLOAT | 4 | R | Start range | [user defined unit]
2209 |  | FLOAT | 4 | R | End range | [user defined unit]
2211 |  | FLOAT | 4 | R | Range Base value | DES = mg/l / ppm PH = pH ORP = mV Fluoride = mg/l / ppm Temperature = °C
2213 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2215 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. e.g. "mg/l"
2219 |  | FLOAT | 4 | R | Sensor signal
2221 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2225 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2227 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2229 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2231 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2233 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2235 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2237 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2238 |  | ASCII | 20 | R | Label | e.g. "Measuring 1"
2248 |  | ASCII | 20 | R | Type of measurement | e.g. "Cl2free"
Measurement 2 | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2300 |  | FLOAT | 4 | R | Measurement
2302 |  | ASCII | 8 | R | Measurement Unit | e.g. "mg/l"
2306 |  | UINT16 | 2 | R | Measurement error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2307 |  | FLOAT | 4 | R | Start range | [user defined unit]
2309 |  | FLOAT | 4 | R | End range | [user defined unit]
2311 |  | FLOAT | 4 | R | Range Base value | DES = mg/l / ppm PH = pH ORP = mV Fluoride = mg/l / ppm Temperature = °C
2313 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2315 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. E.g. "mg/l"
2319 |  | FLOAT | 4 | R | Sensor signal
2321 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2325 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2327 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2329 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2331 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2333 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2335 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2337 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2338 |  | ASCII | 20 | R | Label | e.g. "Measuring 2"
2348 |  | ASCII | 20 | R | Type of measurement | e.g. "Cl2free"
Measurement 3 | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2400 |  | FLOAT | 4 | R | Measurement
2402 |  | ASCII | 8 | R | Measurement Unit | e.g. "mg/l"
2406 |  | UINT16 | 2 | R | Measurement error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2407 |  | FLOAT | 4 | R | Start range | [user defined unit]
2409 |  | FLOAT | 4 | R | End range | [user defined unit]
2411 |  | FLOAT | 4 | R | Range Base value | DES = mg/l / ppm PH = pH ORP = mV Fluoride = mg/l / ppm Temperature = °C
2413 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2415 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. E.g. "mg/l"
2419 |  | FLOAT | 4 | R | Sensor signal
2421 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2425 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2427 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2429 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2431 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2433 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2435 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2437 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2438 |  | ASCII | 20 | R | Label | e.g. "Measuring 3"
2448 |  | ASCII | 20 | R | Type of measurement | e.g. "Cl2free"
Measurement 4 | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2500 |  | FLOAT | 4 | R | Measurement
2502 |  | ASCII | 8 | R | Measurement Unit | e.g. "mg/l"
2506 |  | UINT16 | 2 | R | Measurement error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2507 |  | FLOAT | 4 | R | Start range | [user defined unit]
2509 |  | FLOAT | 4 | R | End range | [user defined unit]
2511 |  | FLOAT | 4 | R | Range Base value | DES = mg/l / ppm PH = pH ORP = mV Fluoride = mg/l / ppm Temperature = °C
2513 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2515 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. E.g. "mg/l"
2519 |  | FLOAT | 4 | R | Sensor signal
2521 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2525 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2527 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2529 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2531 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2533 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2535 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2537 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2538 |  | ASCII | 20 | R | Label | e.g. "Measuring 4"
2548 |  | ASCII | 20 | R | Type of measurement | e.g. "Cl2free"
Measurement 5 | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2600 |  | FLOAT | 4 | R | Measurement
2602 |  | ASCII | 8 | R | Measurement Unit | e.g. "mg/l"
2606 |  | UINT16 | 2 | R | Measurement error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2607 |  | FLOAT | 4 | R | Start range | [user defined unit]
2609 |  | FLOAT | 4 | R | End range | [user defined unit]
2611 |  | FLOAT | 4 | R | Range Base value | DES = mg/l / ppm PH = pH ORP = mV Fluoride = mg/l / ppm Temperature = °C
2613 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2615 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. E.g. "mg/l"
2619 |  | FLOAT | 4 | R | Sensor signal
2621 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2625 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2627 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2629 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2631 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2633 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2635 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2637 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2638 |  | ASCII | 20 | R | Label | e.g. "Measuring 5"
2648 |  | ASCII | 20 | R | Type of measurement | e.g. "Cl2free"
Measurement 6 | [5 empty] | Only the available measurements are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the corresponding registers.
2700 |  | FLOAT | 4 | R | Measurement
2702 |  | ASCII | 8 | R | Measurement Unit | e.g. "mg/l"
2706 |  | UINT16 | 2 | R | Measurement error status | 0 = Inactive 1 = Active (Depending on the type of measurement)
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Calibration error 1 | The distance between the calibration points is too small.
| 2 |  |  |  | Calibration error 2 | Calibration outside of the valid range.
| 3 |  |  |  | Calibration error 3 | Calibration zero point error.
| 4 |  |  |  | Calibration error 4 | Calibration slope error.
| 5 |  |  |  | Calibration error 5 | Zero point missing.
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 1 | Input signal below the measurable range. Mod Con: Voltage too low.
| 9 |  |  |  | Hardware error 2 | Input signal above the measurable range. Mod Con: Current above the measurable range.
| 10 |  |  |  | Hardware error 3 | Hardware error Mod Con: Current below the measurable range.
| 11 |  |  |  | Hardware error 4 | Factory calibration missing. Mod Con: Load error
| 12 |  |  |  | Hardware error 5 | Mod Con: Hardware error
| 13 |  |  |  | Hardware error 6 | Mod Dis: Sensor error Mod Con: Factory calibration is missing
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
2707 |  | FLOAT | 4 | R | Start range | [user defined unit]
2709 |  | FLOAT | 4 | R | End range | [user defined unit]
2711 |  | FLOAT | 4 | R | Range Base value | DES = mg/l / ppm PH = pH ORP = mV Fluoride = mg/l / ppm Temperature = °C
2713 |  | FLOAT | 4 | R | Secondary measurement | Only for chlorine bound.
2715 |  | ASCII | 8 | R | Secondary measurement unit | Only for chlorine bound. e.g. "mg/l"
2719 |  | FLOAT | 4 | R | Sensor signal
2721 |  | ASCII | 8 | R | Sensor signal unit | e.g. "mA"
2725 |  | FLOAT | 4 | RW | Limit value 1 min | [user defined unit]
2727 |  | FLOAT | 4 | RW | Limit value 1 max | [user defined unit]
2729 |  | FLOAT | 4 | RW | Limit value 1 Hysteresis | [user defined unit]
2731 |  | FLOAT | 4 | RW | Limit value 2 min | [user defined unit]
2733 |  | FLOAT | 4 | RW | Limit value 2 max | [user defined unit]
2735 |  | FLOAT | 4 | RW | Limit value 2 Hysteresis | [user defined unit]
2737 |  | UINT16 | 2 | RW | Measurement filter | 0 = Off 1 = Minimum 2 = Light 3 = Medium 4 = Strong
2738 |  | ASCII | 20 | R | Label | e.g. "Measuring 6"
2748 |  | ASCII | 20 | R | Type of measurement | e.g. "Cl2free"
Controller 1 Parameter | [5 empty] | Only the available controllers are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the cor responding registers.
5000 |  | UINT16 | 2 | R | Controller | 0 = Off 1 = On
5001 |  | UINT16 | 2 | R | Controller type | 1 = Proportional 2 = Single feedback control 3 = Compound loop 4 = Dosing contact
5002 |  | UINT16 | 2 | R | Control mode | Only with Compound loop 0 = Single feed forward 1 = Single feed backward 2 = Compound loop
5003 |  | UINT16 | 2 | RW | Operation mode | 0 = Automatic 1 = Manual
5004 |  | UINT16 | 2 | R | Adaption | Only with Single feedback control 1 = Dosing 0% 2 = Wait for X=20% 3 = Dosing 100% 4 = Measuring Dead Time 5 = Measuring Rise Time 6 = Dosing 0% 7 = Done 8 = Abort
5005 |  | UINT16 | 2 | R | Stop reason | 0 = - 1 = Stop / Sample water flow 2 = Stop: Extern stop / DI 3 = Stop: Positioner calibration 4 = Stop: Error measurment signal 5 = Stop / dosing error 6 = Stop: Missing Dosing unit 7 = Stop: Error flow signal 8 = Stop: External Input Error 9 = Stop: Input Ctrl. function 10 = Stop: Container empty 11 = Stop: Container error 12 = Stop: Lockout 13 = Stop: Calib. timeout 14 = Stop: Calibration active 15 = Stop: Boost Dosing 16 = Stop: Max. Dosing Timeout 17 = Stop: No flow 18 = Invalid setpoint
5006 |  | FLOAT | 4 | R | Dosing output | [%]
5008 |  | FLOAT | 4 | R | Controller output | [%]
5010 |  | FLOAT | 4 | R | act. setpoint | [user defined unit], only with Single feedback control, Compound loop and dosing contact
5012 |  | FLOAT | 4 | R | act. dosing factor | [%], only at Proportional control
5014 |  | FLOAT | 4 | RW | Manual dosing | [user defined unit], only in manual mode
5016 |  | UINT32 | 4 | RW | Feed delay time | [seconds]
5018 |  | UINT16 | 2 | R | Control direction | Only with Single feedback control and Compound loop control 0 = direct 1 = inverts
5019 |  | ASCII | 20 | R | Measuring Label | Label of the corresponding measurement
5029 |  | UINT16 | 2 | R | Controller status | 0 = Off 1 = Manual 2 = Automatic 3 = ECO mode 4 = Stopped 5 = hold
5030 |  | UINT16 | 2 | R | reserved
5031 |  | INT32 | 4 | R | reserved
5033 |  | INT32 | 4 | R | reserved
5035 |  | INT32 | 4 | R | reserved
5037 |  | INT32 | 4 | R | reserved
5039 |  | INT16 | 2 | R | reserved
5040 |  | FLOAT | 4 | RW | Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
5042 |  | FLOAT | 4 | RW | Xp | [%], only with Single feedback control
5044 |  | UINT32 | 4 | RW | Tn | [seconds], only with Single feedback control
5046 |  | FLOAT | 4 | RW | reserved
5048 |  | FLOAT | 4 | RW | Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
5050 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
5052 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
5054 |  | FLOAT | 4 | RW | reserved
5056 |  | UINT32 | 4 | RW | Tkonst | [seconds], only with Compound loop control
5058 |  | UINT32 | 4 | RW | Tvar | [seconds], only with Compound loop control
5060 |  | FLOAT | 4 | RW | Max.lin.correction | [%], only with Compound loop control
5062 |  | FLOAT | 4 | RW | Controller factor | Only with Compound loop control.
5064 |  | FLOAT | 4 | RW | Process agent factor | Only with Proportional control.
5066 |  | FLOAT | 4 | RW | Dosing factor | [%], only at Proportional control
5068 |  | FLOAT | 4 | RW | Zero threshold | [%], only with Compound loop control and Proportional control
5070 |  | UINT32 | 4 | RW | Ts | [seconds], only with adaptation
5072 |  | UINT32 | 4 | RW | Tu | [seconds], only with adaptation
5074 |  | INT32 | 4 | R | reserved
5076 |  | INT32 | 4 | R | reserved
5078 |  | INT32 | 4 | R | reserved
5080 |  | FLOAT | 4 | RW | ECO Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
5082 |  | FLOAT | 4 | RW | ECO Xp | [%], only with Single feedback control
5084 |  | UINT32 | 4 | RW | ECO Tn | [seconds], only with Single feedback control
5086 |  | FLOAT | 4 | RW | reserved
5088 |  | FLOAT | 4 | RW | ECO Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
5090 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
5092 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
5094 |  | FLOAT | 4 | RW | reserved
5096 |  | UINT32 | 4 | RW | ECO Tkonst | [seconds], only with Compound loop control
5098 |  | UINT32 | 4 | RW | ECO Tvar | [seconds], only with Compound loop control
5100 |  | FLOAT | 4 | RW | ECO Max.lin.correction | [%], only with Compound loop control
5102 |  | FLOAT | 4 | RW | ECO Controller factor | Only with Compound loop control.
5104 |  | FLOAT | 4 | RW | ECO Process agent factor | Only with Proportional control.
5106 |  | FLOAT | 4 | RW | ECO Dosing factor | [%], only at Proportional control
5108 |  | FLOAT | 4 | RW | ECO Zero threshold | [%], only with Compound loop control and Proportional control
5110 |  | UINT32 | 4 | RW | ECO Ts | [seconds], only with adaptation
5112 |  | UINT32 | 4 | RW | ECO Tu | [seconds], only with adaptation
5114 |  | INT32 | 4 | R | reserved
5116 |  | INT32 | 4 | R | reserved
5118 |  | INT32 | 4 | R | reserved
5120 |  | UINT16 | 2 | R | Boost Dosing | 0 = Off 1 = On
5121 |  | UINT16 | 2 | R | Boost Dosing state | 0 = Inactive 1 = Active 2 = Delay controllers
5122 |  | FLOAT | 4 | RW | Boost Dosing Setpoint | [user defined unit]
5124 |  | UINT32 | 4 | RW | Boost Dosing Dosing duration | [seconds]
5126 |  | UINT16 | 2 | RW | Boost Dosing start | 1 = Boost Dosing started
5127 |  | UINT16 | 2 | RW | Boost Dosing stop | 1 = Boost Dosing stoped
5128 |  | UINT16 | 2 | R | Peak Dosing | 0 = Off 1 = On
5129 |  | UINT16 | 2 | R | Peak Dosing state | 0 = Inactive 1 = Raise 2 = Active 3 = Standby
5130 |  | FLOAT | 4 | RW | Peak Dosing Setpoint | [user defined unit]
5132 |  | UINT32 | 4 | RW | Peak Dosing Dosing duration | [seconds]
5134 |  | UINT16 | 2 | RW | Peak Dosing start | 1 = Peck Dosing started
5135 |  | UINT16 | 2 | RW | Peak Dosing stop | 1 = Peck Dosing stoped
Controller 1 Actuator / Dosing
5300 |  | UINT16 | 2 | R | Actuator Type | 101 = Positioner w. Ym 102 = Positioner wo. Ym 103 = Pump 2P 104 = Dosing contact 105 = Analog output 2P 106 = Analog output 3P (single) 107 = Analog output 3P (dual) 108 = Pump 3P
5301 |  | UINT16 | 2 | R | Actuator Status (Increase) | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
5302 |  | UINT16 | 2 | R | Actuator Range (Increase) | Only with Analog output 2P and Analog output 3P (single) 0 = 0...20 1 = 4...20
5303 |  | UINT16 | 2 | R | Actuator Pump type (Increase) | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
5304 |  | UINT16 | 2 | R | Actuator max. Pulse/Min (Increase) | Only with Pump type Solenoid pump. e.g. 120
5305 |  | UINT32 | 4 | R | Actuator Tp (Increase) | [seconds], only with pump type dosing pump
5307 |  | UINT16 | 2 | R | Actuator Status Decrease | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
5308 |  | UINT16 | 2 | R | Actuator Range Decrease | [%], only with Analog output 3P (dual) 0 = 0...20 1 = 4...20
5309 |  | UINT16 | 2 | R | Actuator Pump type Decrease | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
5310 |  | UINT16 | 2 | R | Actuator max. Pulse/Min Decrease | Only with Pump type Solenoid pump. e.g. 120
5311 |  | UINT32 | 4 | R | Actuator Tp Decrease | [seconds], only with pump type dosing pump
5313 |  | UINT32 | 4 | R | Actuator Ty | [seconds.] ,only for positioner without Ym
5315 |  | FLOAT | 4 | R | Actuator Feedback Tolerance | [%], only for positioner with Ym
5317 |  | FLOAT | 4 | R | Actuator Feedback | [%], only for positioner with Ym
5319 |  | INT32 | 4 | R | reserved
5321 |  | INT32 | 4 | R | reserved
5323 |  | FLOAT | 4 | R | Consumption fo dosing agent (Increase) | [user defined unit], e.g. 91.6 l.
5325 |  | FLOAT | 4 | R | Current dosing (Increase) | [user defined unit], e.g. 0.5 l/h.
5327 |  | FLOAT | 4 | R | reserved
5329 |  | FLOAT | 4 | R | reserved
5331 |  | FLOAT | 4 | R | Average dosing of dosing agent (Increase) | [user defined unit], e.g. 10.3 l/h.
5333 |  | ASCII | 8 | R | Rate unit (Increase) | e.g. "l/h"
5337 |  | UINT16 | 2 | RW | reserved
5338 |  | FLOAT | 4 | R | Consumption fo dosing agent Decrease | [user defined unit], e.g. 91.6 l.
5340 |  | FLOAT | 4 | R | Current dosing Decrease | [user defined unit], e.g. 0.5 l/h.
5342 |  | FLOAT | 4 | R | reserved
5344 |  | FLOAT | 4 | R | reserved
5346 |  | FLOAT | 4 | R | Average dosing of dosing agent Decrease | [user defined unit], e.g. 10.3 l/h.
5348 |  | ASCII | 8 | R | Rate unit Decrease | e.g. "l/h"
5352 |  | UINT16 | 2 | RW | reserved
5353 |  | INT32 | 4 | R | reserved
5355 |  | INT32 | 4 | R | reserved
5357 |  | UINT16 | 2 | R | Canister monitoring (Increase) | 0 = Off 1 = On
5358 |  | UINT16 | 2 | R | Canister monitoring state (Increase) | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
5359 |  | FLOAT | 4 | RW | Canister monitoring capacity (Increase) | [user defined unit], e.g. 50 kg.
5361 |  | FLOAT | 4 | R | Canister monitoring remaining capacity (Increase) | [user defined unit], e.g. 25 kg.
5363 |  | ASCII | 8 | R | Canister monitoring unit (Increase) | e.g. "kg"
5367 |  | UINT16 | 2 | R | Canister monitoring Decrease | 0 = Off 1 = On
5368 |  | UINT16 | 2 | R | Canister monitoring state Decrease | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
5369 |  | FLOAT | 4 | RW | Canister monitoring capacity Decrease | [user defined unit], e.g. 50 kg.
5371 |  | FLOAT | 4 | R | Canister monitoring remaining capacity Decrease | [user defined unit], e.g. 25 kg.
5373 |  | ASCII | 8 | R | Canister monitoring unit Decrease | e.g. "kg"
Controller 2 Parameter | [5 empty] | Only the available controllers are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the cor responding registers.
5500 |  | UINT16 | 2 | R | Controller | 0 = Off 1 = On
5501 |  | UINT16 | 2 | R | Controller type | 1 = Proportional 2 = Single feedback control 3 = Compound loop 4 = Dosing contact
5502 |  | UINT16 | 2 | R | Control mode | Only with Compound loop 0 = Single feed forward 1 = Single feed backward 2 = Compound loop
5503 |  | UINT16 | 2 | RW | Operation mode | 0 = Automatic 1 = Manual
5504 |  | UINT16 | 2 | R | Adaption | Only with Single feedback control 1 = Dosing 0% 2 = Wait for X=20% 3 = Dosing 100% 4 = Measuring Dead Time 5 = Measuring Rise Time 6 = Dosing 0% 7 = Done 8 = Abort
5505 |  | UINT16 | 2 | R | Stop reason | 0 = - 1 = Stop / Sample water flow 2 = Stop: Extern stop / DI 3 = Stop: Positioner calibration 4 = Stop: Error measurment signal 5 = Stop / dosing error 6 = Stop: Missing Dosing unit 7 = Stop: Error flow signal 8 = Stop: External Input Error 9 = Stop: Input Ctrl. function 10 = Stop: Container empty 11 = Stop: Container error 12 = Stop: Lockout 13 = Stop: Calib. timeout 14 = Stop: Calibration active 15 = Stop: Boost Dosing 16 = Stop: Max. Dosing Timeout 17 = Stop: No flow 18 = Invalid setpoint
5506 |  | FLOAT | 4 | R | Dosing output | [%]
5508 |  | FLOAT | 4 | R | Controller output | [%]
5510 |  | FLOAT | 4 | R | act. setpoint | [user defined unit], only with Single feedback control, Compound loop and dosing contact
5512 |  | FLOAT | 4 | R | act. dosing factor | [%], only at Proportional control
5514 |  | FLOAT | 4 | RW | Manual dosing | [user defined unit], only in manual mode
5516 |  | UINT32 | 4 | RW | Feed delay time | [seconds]
5518 |  | UINT16 | 2 | R | Control direction | Only with Single feedback control and Compound loop control 0 = direct 1 = inverts
5519 |  | ASCII | 20 | R | Measuring Label | Label of the corresponding measurement
5529 |  | UINT16 | 2 | R | Controller status | 0 = Off 1 = Manual 2 = Automatic 3 = ECO mode 4 = Stopped 5 = hold
5530 |  | UINT16 | 2 | R | reserved
5531 |  | INT32 | 4 | R | reserved
5533 |  | INT32 | 4 | R | reserved
5535 |  | INT32 | 4 | R | reserved
5537 |  | INT32 | 4 | R | reserved
5539 |  | INT16 | 2 | R | reserved
5540 |  | FLOAT | 4 | RW | Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
5542 |  | FLOAT | 4 | RW | Xp | [%], only with Single feedback control
5544 |  | UINT32 | 4 | RW | Tn | [seconds], only with Single feedback control
5546 |  | FLOAT | 4 | RW | reserved
5548 |  | FLOAT | 4 | RW | Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
5550 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
5552 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
5554 |  | FLOAT | 4 | RW | reserved
5556 |  | UINT32 | 4 | RW | Tkonst | [seconds], only with Compound loop control
5558 |  | UINT32 | 4 | RW | Tvar | [seconds], only with Compound loop control
5560 |  | FLOAT | 4 | RW | Max.lin.correction | [%], only with Compound loop control
5562 |  | FLOAT | 4 | RW | Controller factor | Only with Compound loop control.
5564 |  | FLOAT | 4 | RW | Process agent factor | Only with Proportional control.
5566 |  | FLOAT | 4 | RW | Dosing factor | [%], only at Proportional control
5568 |  | FLOAT | 4 | RW | Zero threshold | [%], only with Compound loop control and Proportional control
5570 |  | UINT32 | 4 | RW | Ts | [seconds], only with adaptation
5572 |  | UINT32 | 4 | RW | Tu | [seconds], only with adaptation
5574 |  | INT32 | 4 | R | reserved
5576 |  | INT32 | 4 | R | reserved
5578 |  | INT32 | 4 | R | reserved
5580 |  | FLOAT | 4 | RW | ECO Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
5582 |  | FLOAT | 4 | RW | ECO Xp | [%], only with Single feedback control
5584 |  | UINT32 | 4 | RW | ECO Tn | [seconds], only with Single feedback control
5586 |  | FLOAT | 4 | RW | reserved
5588 |  | FLOAT | 4 | RW | ECO Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
5590 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
5592 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
5594 |  | FLOAT | 4 | RW | reserved
5596 |  | UINT32 | 4 | RW | ECO Tkonst | [seconds], only with Compound loop control
5598 |  | UINT32 | 4 | RW | ECO Tvar | [seconds], only with Compound loop control
5600 |  | FLOAT | 4 | RW | ECO Max.lin.correction | [%], only with Compound loop control
5602 |  | FLOAT | 4 | RW | ECO Controller factor | Only with Compound loop control.
5604 |  | FLOAT | 4 | RW | ECO Process agent factor | Only with Proportional control.
5606 |  | FLOAT | 4 | RW | ECO Dosing factor | [%], only at Proportional control
5608 |  | FLOAT | 4 | RW | ECO Zero threshold | [%], only with Compound loop control and Proportional control
5610 |  | UINT32 | 4 | RW | ECO Ts | [seconds], only with adaptation
5612 |  | UINT32 | 4 | RW | ECO Tu | [seconds], only with adaptation
5614 |  | INT32 | 4 | R | reserved
5616 |  | INT32 | 4 | R | reserved
5618 |  | INT32 | 4 | R | reserved
5620 |  | UINT16 | 2 | R | Boost Dosing | 0 = Off 1 = On
5621 |  | UINT16 | 2 | R | Boost Dosing state | 0 = Inactive 1 = Active 2 = Delay controllers
5622 |  | FLOAT | 4 | RW | Boost Dosing Setpoint | [user defined unit]
5624 |  | UINT32 | 4 | RW | Boost Dosing Dosing duration | [seconds]
5626 |  | UINT16 | 2 | RW | Boost Dosing start | 1 = Boost Dosing started
5627 |  | UINT16 | 2 | RW | Boost Dosing stop | 1 = Boost Dosing stoped
5628 |  | UINT16 | 2 | R | Peak Dosing | 0 = Off 1 = On
5629 |  | UINT16 | 2 | R | Peak Dosing state | 0 = Inactive 1 = Raise 2 = Active 3 = Standby
5630 |  | FLOAT | 4 | RW | Peak Dosing Setpoint | [user defined unit]
5632 |  | UINT32 | 4 | RW | Peak Dosing Dosing duration | [seconds]
5634 |  | UINT16 | 2 | RW | Peak Dosing start | 1 = Peck Dosing started
5635 |  | UINT16 | 2 | RW | Peak Dosing stop | 1 = Peck Dosing stoped
Controller 2 Actuator / Dosing
5800 |  | UINT16 | 2 | R | Actuator Type | 101 = Positioner w. Ym 102 = Positioner wo. Ym 103 = Pump 2P 104 = Dosing contact 105 = Analog output 2P 106 = Analog output 3P (single) 107 = Analog output 3P (dual) 108 = Pump 3P
5801 |  | UINT16 | 2 | R | Actuator Status (Increase) | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
5802 |  | UINT16 | 2 | R | Actuator Range (Increase) | Only with Analog output 2P and Analog output 3P (single) 0 = 0...20 1 = 4...20
5803 |  | UINT16 | 2 | R | Actuator Pump type (Increase) | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
5804 |  | UINT16 | 2 | R | Actuator max. Pulse/Min (Increase) | Only with Pump type Solenoid pump. e.g. 120
5805 |  | UINT32 | 4 | R | Actuator Tp (Increase) | [seconds], only with pump type dosing pump
5807 |  | UINT16 | 2 | R | Actuator Status Decrease | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
5808 |  | UINT16 | 2 | R | Actuator Range Decrease | [%], only with Analog output 3P (dual) 0 = 0...20 1 = 4...20
5809 |  | UINT16 | 2 | R | Actuator Pump type Decrease | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
5810 |  | UINT16 | 2 | R | Actuator max. Pulse/Min Decrease | Only with Pump type Solenoid pump. e.g. 120
5811 |  | UINT32 | 4 | R | Actuator Tp Decrease | [seconds], only with pump type dosing pump
5813 |  | UINT32 | 4 | R | Actuator Ty | [seconds.] ,only for positioner without Ym
5815 |  | FLOAT | 4 | R | Actuator Feedback Tolerance | [%], only for positioner with Ym
5817 |  | FLOAT | 4 | R | Actuator Feedback | [%], only for positioner with Ym
5819 |  | INT32 | 4 | R | reserved
5821 |  | INT32 | 4 | R | reserved
5823 |  | FLOAT | 4 | R | Consumption fo dosing agent (Increase) | [user defined unit], e.g. 91.6 l.
5825 |  | FLOAT | 4 | R | Current dosing (Increase) | [user defined unit], e.g. 0.5 l/h.
5827 |  | FLOAT | 4 | R | reserved
5829 |  | FLOAT | 4 | R | reserved
5831 |  | FLOAT | 4 | R | Average dosing of dosing agent (Increase) | [user defined unit], e.g. 10.3 l/h.
5833 |  | ASCII | 8 | R | Rate unit (Increase) | e.g. "l/h"
5837 |  | UINT16 | 2 | RW | reserved
5838 |  | FLOAT | 4 | R | Consumption fo dosing agent Decrease | [user defined unit], e.g. 91.6 l.
5840 |  | FLOAT | 4 | R | Current dosing Decrease | [user defined unit], e.g. 0.5 l/h.
5842 |  | FLOAT | 4 | R | reserved
5844 |  | FLOAT | 4 | R | reserved
5846 |  | FLOAT | 4 | R | Average dosing of dosing agent Decrease | [user defined unit], e.g. 10.3 l/h.
5848 |  | ASCII | 8 | R | Rate unit Decrease | e.g. "l/h"
5852 |  | UINT16 | 2 | RW | reserved
5853 |  | INT32 | 4 | R | reserved
5855 |  | INT32 | 4 | R | reserved
5857 |  | UINT16 | 2 | R | Canister monitoring (Increase) | 0 = Off 1 = On
5858 |  | UINT16 | 2 | R | Canister monitoring state (Increase) | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
5859 |  | FLOAT | 4 | RW | Canister monitoring capacity (Increase) | [user defined unit], e.g. 50 kg.
5861 |  | FLOAT | 4 | R | Canister monitoring remaining capacity (Increase) | [user defined unit], e.g. 25 kg.
5863 |  | ASCII | 8 | R | Canister monitoring unit (Increase) | e.g. "kg"
5867 |  | UINT16 | 2 | R | Canister monitoring Decrease | 0 = Off 1 = On
5868 |  | UINT16 | 2 | R | Canister monitoring state Decrease | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
5869 |  | FLOAT | 4 | RW | Canister monitoring capacity Decrease | [user defined unit], e.g. 50 kg.
5871 |  | FLOAT | 4 | R | Canister monitoring remaining capacity Decrease | [user defined unit], e.g. 25 kg.
5873 |  | ASCII | 8 | R | Canister monitoring unit Decrease | e.g. "kg"
Controller 3 Parameter | [5 empty] | Only the available controllers are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the cor responding registers.
6000 |  | UINT16 | 2 | R | Controller | 0 = Off 1 = On
6001 |  | UINT16 | 2 | R | Controller type | 1 = Proportional 2 = Single feedback control 3 = Compound loop 4 = Dosing contact
6002 |  | UINT16 | 2 | R | Control mode | Only with Compound loop 0 = Single feed forward 1 = Single feed backward 2 = Compound loop
6003 |  | UINT16 | 2 | RW | Operation mode | 0 = Automatic 1 = Manual
6004 |  | UINT16 | 2 | R | Adaption | Only with Single feedback control 1 = Dosing 0% 2 = Wait for X=20% 3 = Dosing 100% 4 = Measuring Dead Time 5 = Measuring Rise Time 6 = Dosing 0% 7 = Done 8 = Abort
6005 |  | UINT16 | 2 | R | Stop reason | 0 = - 1 = Stop / Sample water flow 2 = Stop: Extern stop / DI 3 = Stop: Positioner calibration 4 = Stop: Error measurment signal 5 = Stop / dosing error 6 = Stop: Missing Dosing unit 7 = Stop: Error flow signal 8 = Stop: External Input Error 9 = Stop: Input Ctrl. function 10 = Stop: Container empty 11 = Stop: Container error 12 = Stop: Lockout 13 = Stop: Calib. timeout 14 = Stop: Calibration active 15 = Stop: Boost Dosing 16 = Stop: Max. Dosing Timeout 17 = Stop: No flow 18 = Invalid setpoint
6006 |  | FLOAT | 4 | R | Dosing output | [%]
6008 |  | FLOAT | 4 | R | Controller output | [%]
6010 |  | FLOAT | 4 | R | act. setpoint | [user defined unit], only with Single feedback control, Compound loop and dosing contact
6012 |  | FLOAT | 4 | R | act. dosing factor | [%], only at Proportional control
6014 |  | FLOAT | 4 | RW | Manual dosing | [user defined unit], only in manual mode
6016 |  | UINT32 | 4 | RW | Feed delay time | [seconds]
6018 |  | UINT16 | 2 | R | Control direction | Only with Single feedback control and Compound loop control 0 = direct 1 = inverts
6019 |  | ASCII | 20 | R | Measuring Label | Label of the corresponding measurement
6029 |  | UINT16 | 2 | R | Controller status | 0 = Off 1 = Manual 2 = Automatic 3 = ECO mode 4 = Stopped 5 = hold
6030 |  | UINT16 | 2 | R | reserved
6031 |  | INT32 | 4 | R | reserved
6033 |  | INT32 | 4 | R | reserved
6035 |  | INT32 | 4 | R | reserved
6037 |  | INT32 | 4 | R | reserved
6039 |  | INT16 | 2 | R | reserved
6040 |  | FLOAT | 4 | RW | Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
6042 |  | FLOAT | 4 | RW | Xp | [%], only with Single feedback control
6044 |  | UINT32 | 4 | RW | Tn | [seconds], only with Single feedback control
6046 |  | FLOAT | 4 | RW | reserved
6048 |  | FLOAT | 4 | RW | Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
6050 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
6052 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
6054 |  | FLOAT | 4 | RW | reserved
6056 |  | UINT32 | 4 | RW | Tkonst | [seconds], only with Compound loop control
6058 |  | UINT32 | 4 | RW | Tvar | [seconds], only with Compound loop control
6060 |  | FLOAT | 4 | RW | Max.lin.correction | [%], only with Compound loop control
6062 |  | FLOAT | 4 | RW | Controller factor | Only with Compound loop control.
6064 |  | FLOAT | 4 | RW | Process agent factor | Only with Proportional control.
6066 |  | FLOAT | 4 | RW | Dosing factor | [%], only at Proportional control
6068 |  | FLOAT | 4 | RW | Zero threshold | [%], only with Compound loop control and Proportional control
6070 |  | UINT32 | 4 | RW | Ts | [seconds], only with adaptation
6072 |  | UINT32 | 4 | RW | Tu | [seconds], only with adaptation
6074 |  | INT32 | 4 | R | reserved
6076 |  | INT32 | 4 | R | reserved
6078 |  | INT32 | 4 | R | reserved
6080 |  | FLOAT | 4 | RW | ECO Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
6082 |  | FLOAT | 4 | RW | ECO Xp | [%], only with Single feedback control
6084 |  | UINT32 | 4 | RW | ECO Tn | [seconds], only with Single feedback control
6086 |  | FLOAT | 4 | RW | reserved
6088 |  | FLOAT | 4 | RW | ECO Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
6090 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
6092 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
6094 |  | FLOAT | 4 | RW | reserved
6096 |  | UINT32 | 4 | RW | ECO Tkonst | [seconds], only with Compound loop control
6098 |  | UINT32 | 4 | RW | ECO Tvar | [seconds], only with Compound loop control
6100 |  | FLOAT | 4 | RW | ECO Max.lin.correction | [%], only with Compound loop control
6102 |  | FLOAT | 4 | RW | ECO Controller factor | Only with Compound loop control.
6104 |  | FLOAT | 4 | RW | ECO Process agent factor | Only with Proportional control.
6106 |  | FLOAT | 4 | RW | ECO Dosing factor | [%], only at Proportional control
6108 |  | FLOAT | 4 | RW | ECO Zero threshold | [%], only with Compound loop control and Proportional control
6110 |  | UINT32 | 4 | RW | ECO Ts | [seconds], only with adaptation
6112 |  | UINT32 | 4 | RW | ECO Tu | [seconds], only with adaptation
6114 |  | INT32 | 4 | R | reserved
6116 |  | INT32 | 4 | R | reserved
6118 |  | INT32 | 4 | R | reserved
6120 |  | UINT16 | 2 | R | Boost Dosing | 0 = Off 1 = On
6121 |  | UINT16 | 2 | R | Boost Dosing state | 0 = Inactive 1 = Active 2 = Delay controllers
6122 |  | FLOAT | 4 | RW | Boost Dosing Setpoint | [user defined unit]
6124 |  | UINT32 | 4 | RW | Boost Dosing Dosing duration | [seconds]
6126 |  | UINT16 | 2 | RW | Boost Dosing start | 1 = Boost Dosing started
6127 |  | UINT16 | 2 | RW | Boost Dosing stop | 1 = Boost Dosing stoped
6128 |  | UINT16 | 2 | R | Peak Dosing | 0 = Off 1 = On
6129 |  | UINT16 | 2 | R | Peak Dosing state | 0 = Inactive 1 = Raise 2 = Active 3 = Standby
6130 |  | FLOAT | 4 | RW | Peak Dosing Setpoint | [user defined unit]
6132 |  | UINT32 | 4 | RW | Peak Dosing Dosing duration | [seconds]
6134 |  | UINT16 | 2 | RW | Peak Dosing start | 1 = Peck Dosing started
6135 |  | UINT16 | 2 | RW | Peak Dosing stop | 1 = Peck Dosing stoped
Controller 3 Actuator / Dosing
6300 |  | UINT16 | 2 | R | Actuator Type | 101 = Positioner w. Ym 102 = Positioner wo. Ym 103 = Pump 2P 104 = Dosing contact 105 = Analog output 2P 106 = Analog output 3P (single) 107 = Analog output 3P (dual) 108 = Pump 3P
6301 |  | UINT16 | 2 | R | Actuator Status (Increase) | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
6302 |  | UINT16 | 2 | R | Actuator Range (Increase) | Only with Analog output 2P and Analog output 3P (single) 0 = 0...20 1 = 4...20
6303 |  | UINT16 | 2 | R | Actuator Pump type (Increase) | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
6304 |  | UINT16 | 2 | R | Actuator max. Pulse/Min (Increase) | Only with Pump type Solenoid pump. e.g. 120
6305 |  | UINT32 | 4 | R | Actuator Tp (Increase) | [seconds], only with pump type dosing pump
6307 |  | UINT16 | 2 | R | Actuator Status Decrease | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
6308 |  | UINT16 | 2 | R | Actuator Range Decrease | [%], only with Analog output 3P (dual) 0 = 0...20 1 = 4...20
6309 |  | UINT16 | 2 | R | Actuator Pump type Decrease | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
6310 |  | UINT16 | 2 | R | Actuator max. Pulse/Min Decrease | Only with Pump type Solenoid pump. e.g. 120
6311 |  | UINT32 | 4 | R | Actuator Tp Decrease | [seconds], only with pump type dosing pump
6313 |  | UINT32 | 4 | R | Actuator Ty | [seconds.] ,only for positioner without Ym
6315 |  | FLOAT | 4 | R | Actuator Feedback Tolerance | Only for positioner with Ym in%.
6317 |  | FLOAT | 4 | R | Actuator Feedback | [%], only for positioner with Ym
6319 |  | INT32 | 4 | R | reserved
6321 |  | INT32 | 4 | R | reserved
6323 |  | FLOAT | 4 | R | Consumption fo dosing agent (Increase) | [user defined unit], e.g. 91.6 l.
6325 |  | FLOAT | 4 | R | Current dosing (Increase) | [user defined unit], e.g. 0.5 l/h.
6327 |  | FLOAT | 4 | R | reserved
6329 |  | FLOAT | 4 | R | reserved
6331 |  | FLOAT | 4 | R | Average dosing of dosing agent (Increase) | [user defined unit], e.g. 10.3 l/h.
6333 |  | ASCII | 8 | R | Rate unit (Increase) | e.g. "l/h"
6337 |  | UINT16 | 2 | RW | reserved
6338 |  | FLOAT | 4 | R | Consumption fo dosing agent Decrease | [user defined unit], e.g. 91.6 l.
6340 |  | FLOAT | 4 | R | Current dosing Decrease | [user defined unit], e.g. 0.5 l/h.
6342 |  | FLOAT | 4 | R | reserved
6344 |  | FLOAT | 4 | R | reserved
6346 |  | FLOAT | 4 | R | Average dosing of dosing agent Decrease | [user defined unit], e.g. 10.3 l/h.
6348 |  | ASCII | 8 | R | Rate unit Decrease | e.g. "l/h"
6352 |  | UINT16 | 2 | RW | reserved
6353 |  | INT32 | 4 | R | reserved
6355 |  | INT32 | 4 | R | reserved
6357 |  | UINT16 | 2 | R | Canister monitoring (Increase) | 0 = Off 1 = On
6358 |  | UINT16 | 2 | R | Canister monitoring state (Increase) | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
6359 |  | FLOAT | 4 | RW | Canister monitoring capacity (Increase) | [user defined unit], e.g. 50 kg.
6361 |  | FLOAT | 4 | R | Canister monitoring remaining capacity (Increase) | [user defined unit], e.g. 25 kg.
6363 |  | ASCII | 8 | R | Canister monitoring unit (Increase) | e.g. "kg"
6367 |  | UINT16 | 2 | R | Canister monitoring Decrease | 0 = Off 1 = On
6368 |  | UINT16 | 2 | R | Canister monitoring state Decrease | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
6369 |  | FLOAT | 4 | RW | Canister monitoring capacity Decrease | [user defined unit], e.g. 50 kg.
6371 |  | FLOAT | 4 | R | Canister monitoring remaining capacity Decrease | [user defined unit], e.g. 25 kg.
6373 |  | ASCII | 8 | R | Canister monitoring unit Decrease | e.g. "kg"
Controller 4 Parameter | [5 empty] | Only the available controllers are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the cor responding registers.
6500 |  | UINT16 | 2 | R | Controller | 0 = Off 1 = On
6501 |  | UINT16 | 2 | R | Controller type | 1 = Proportional 2 = Single feedback control 3 = Compound loop 4 = Dosing contact
6502 |  | UINT16 | 2 | R | Control mode | Only with Compound loop 0 = Single feed forward 1 = Single feed backward 2 = Compound loop
6503 |  | UINT16 | 2 | RW | Operation mode | 0 = Automatic 1 = Manual
6504 |  | UINT16 | 2 | R | Adaption | Only with Single feedback control 1 = Dosing 0% 2 = Wait for X=20% 3 = Dosing 100% 4 = Measuring Dead Time 5 = Measuring Rise Time 6 = Dosing 0% 7 = Done 8 = Abort
6505 |  | UINT16 | 2 | R | Stop reason | 0 = - 1 = Stop / Sample water flow 2 = Stop: Extern stop / DI 3 = Stop: Positioner calibration 4 = Stop: Error measurment signal 5 = Stop / dosing error 6 = Stop: Missing Dosing unit 7 = Stop: Error flow signal 8 = Stop: External Input Error 9 = Stop: Input Ctrl. function 10 = Stop: Container empty 11 = Stop: Container error 12 = Stop: Lockout 13 = Stop: Calib. timeout 14 = Stop: Calibration active 15 = Stop: Boost Dosing 16 = Stop: Max. Dosing Timeout 17 = Stop: No flow 18 = Invalid setpoint
6506 |  | FLOAT | 4 | R | Dosing output | [%]
6508 |  | FLOAT | 4 | R | Controller output | [%]
6510 |  | FLOAT | 4 | R | act. setpoint | [user defined unit], only with Single feedback control, Compound loop and dosing contact
6512 |  | FLOAT | 4 | R | act. dosing factor | [%], only at Proportional control
6514 |  | FLOAT | 4 | RW | Manual dosing | [user defined unit], only in manual mode
6516 |  | UINT32 | 4 | RW | Feed delay time | [seconds]
6518 |  | UINT16 | 2 | R | Control direction | Only with Single feedback control and Compound loop control 0 = direct 1 = inverts
6519 |  | ASCII | 20 | R | Measuring Label | Label of the corresponding measurement
6529 |  | UINT16 | 2 | R | Controller status | 0 = Off 1 = Manual 2 = Automatic 3 = ECO mode 4 = Stopped 5 = hold
6530 |  | UINT16 | 2 | R | reserved
6531 |  | INT32 | 4 | R | reserved
6533 |  | INT32 | 4 | R | reserved
6535 |  | INT32 | 4 | R | reserved
6537 |  | INT32 | 4 | R | reserved
6539 |  | INT16 | 2 | R | reserved
6540 |  | FLOAT | 4 | RW | Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
6542 |  | FLOAT | 4 | RW | Xp | [%], only with Single feedback control
6544 |  | UINT32 | 4 | RW | Tn | [seconds], only with Single feedback control
6546 |  | FLOAT | 4 | RW | reserved
6548 |  | FLOAT | 4 | RW | Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
6550 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
6552 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
6554 |  | FLOAT | 4 | RW | reserved
6556 |  | UINT32 | 4 | RW | Tkonst | [seconds], only with Compound loop control
6558 |  | UINT32 | 4 | RW | Tvar | [seconds], only with Compound loop control
6560 |  | FLOAT | 4 | RW | Max.lin.correction | [%], only with Compound loop control
6562 |  | FLOAT | 4 | RW | Controller factor | Only with Compound loop control.
6564 |  | FLOAT | 4 | RW | Process agent factor | Only with Proportional control.
6566 |  | FLOAT | 4 | RW | Dosing factor | [%], only at Proportional control
6568 |  | FLOAT | 4 | RW | Zero threshold | [%], only with Compound loop control and Proportional control
6570 |  | UINT32 | 4 | RW | Ts | [seconds], only with adaptation
6572 |  | UINT32 | 4 | RW | Tu | [seconds], only with adaptation
6574 |  | INT32 | 4 | R | reserved
6576 |  | INT32 | 4 | R | reserved
6578 |  | INT32 | 4 | R | reserved
6580 |  | FLOAT | 4 | RW | ECO Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
6582 |  | FLOAT | 4 | RW | ECO Xp | [%], only with Single feedback control
6584 |  | UINT32 | 4 | RW | ECO Tn | [seconds], only with Single feedback control
6586 |  | FLOAT | 4 | RW | reserved
6588 |  | FLOAT | 4 | RW | ECO Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
6590 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
6592 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
6594 |  | FLOAT | 4 | RW | reserved
6596 |  | UINT32 | 4 | RW | ECO Tkonst | [seconds], only with Compound loop control
6598 |  | UINT32 | 4 | RW | ECO Tvar | [seconds], only with Compound loop control
6600 |  | FLOAT | 4 | RW | ECO Max.lin.correction | [%], only with Compound loop control
6602 |  | FLOAT | 4 | RW | ECO Controller factor | Only with Compound loop control.
6604 |  | FLOAT | 4 | RW | ECO Process agent factor | Only with Proportional control.
6606 |  | FLOAT | 4 | RW | ECO Dosing factor | [%], only at Proportional control
6608 |  | FLOAT | 4 | RW | ECO Zero threshold | [%], only with Compound loop control and Proportional control
6610 |  | UINT32 | 4 | RW | ECO Ts | [seconds], only with adaptation
6612 |  | UINT32 | 4 | RW | ECO Tu | [seconds], only with adaptation
6614 |  | INT32 | 4 | R | reserved
6616 |  | INT32 | 4 | R | reserved
6618 |  | INT32 | 4 | R | reserved
6620 |  | UINT16 | 2 | R | Boost Dosing | 0 = Off 1 = On
6621 |  | UINT16 | 2 | R | Boost Dosing state | 0 = Inactive 1 = Active 2 = Delay controllers
6622 |  | FLOAT | 4 | RW | Boost Dosing Setpoint | [user defined unit]
6624 |  | UINT32 | 4 | RW | Boost Dosing Dosing duration | [seconds]
6626 |  | UINT16 | 2 | RW | Boost Dosing start | 1 = Boost Dosing started
6627 |  | UINT16 | 2 | RW | Boost Dosing stop | 1 = Boost Dosing stoped
6628 |  | UINT16 | 2 | R | Peak Dosing | 0 = Off 1 = On
6629 |  | UINT16 | 2 | R | Peak Dosing state | 0 = Inactive 1 = Raise 2 = Active 3 = Standby
6630 |  | FLOAT | 4 | RW | Peak Dosing Setpoint | [user defined unit]
6632 |  | UINT32 | 4 | RW | Peak Dosing Dosing duration | [seconds]
6634 |  | UINT16 | 2 | RW | Peak Dosing start | 1 = Peck Dosing started
6635 |  | UINT16 | 2 | RW | Peak Dosing stop | 1 = Peck Dosing stoped
Controller 4 Actuator/ Dosing
6800 |  | UINT16 | 2 | R | Actuator Type | 101 = Positioner w. Ym 102 = Positioner wo. Ym 103 = Pump 2P 104 = Dosing contact 105 = Analog output 2P 106 = Analog output 3P (single) 107 = Analog output 3P (dual) 108 = Pump 3P
6801 |  | UINT16 | 2 | R | Actuator Status (Increase) | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
6802 |  | UINT16 | 2 | R | Actuator Range (Increase) | Only with Analog output 2P and Analog output 3P (single) 0 = 0...20 1 = 4...20
6803 |  | UINT16 | 2 | R | Actuator Pump type (Increase) | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
6804 |  | UINT16 | 2 | R | Actuator max. Pulse/Min (Increase) | Only with Pump type Solenoid pump. e.g. 120
6805 |  | UINT32 | 4 | R | Actuator Tp (Increase) | [seconds], only with pump type dosing pump
6807 |  | UINT16 | 2 | R | Actuator Status Decrease | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
6808 |  | UINT16 | 2 | R | Actuator Range Decrease | [%], only with Analog output 3P (dual) 0 = 0...20 1 = 4...20
6809 |  | UINT16 | 2 | R | Actuator Pump type Decrease | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
6810 |  | UINT16 | 2 | R | Actuator max. Pulse/Min Decrease | Only with Pump type Solenoid pump. e.g. 120
6811 |  | UINT32 | 4 | R | Actuator Tp Decrease | [seconds], only with pump type dosing pump
6813 |  | UINT32 | 4 | R | Actuator Ty | [seconds], only for positioner without Ym
6815 |  | FLOAT | 4 | R | Actuator Feedback Tolerance | [%], only for positioner with Ym
6817 |  | FLOAT | 4 | R | Actuator Feedback | [%], only for positioner with Ym
6819 |  | INT32 | 4 | R | reserved
6821 |  | INT32 | 4 | R | reserved
6823 |  | FLOAT | 4 | R | Consumption fo dosing agent (Increase) | [user defined unit], e.g. 91.6 l.
6825 |  | FLOAT | 4 | R | Current dosing (Increase) | [user defined unit], e.g. 0.5 l/h.
6827 |  | FLOAT | 4 | R | reserved
6829 |  | FLOAT | 4 | R | reserved
6831 |  | FLOAT | 4 | R | Average dosing of dosing agent (Increase) | [user defined unit], e.g. 10.3 l/h.
6833 |  | ASCII | 8 | R | Rate unit (Increase) | e.g. "l/h"
6837 |  | UINT16 | 2 | RW | reserved
6838 |  | FLOAT | 4 | R | Consumption fo dosing agent Decrease | [user defined unit], e.g. 91.6 l.
6840 |  | FLOAT | 4 | R | Current dosing Decrease | [user defined unit], e.g. 0.5 l/h.
6842 |  | FLOAT | 4 | R | reserved
6844 |  | FLOAT | 4 | R | reserved
6846 |  | FLOAT | 4 | R | Average dosing of dosing agent Decrease | [user defined unit], e.g. 10.3 l/h.
6848 |  | ASCII | 8 | R | Rate unit Decrease | e.g. "l/h"
6852 |  | UINT16 | 2 | RW | reserved
6853 |  | INT32 | 4 | R | reserved
6855 |  | INT32 | 4 | R | reserved
6857 |  | UINT16 | 2 | R | Canister monitoring (Increase) | 0 = Off 1 = On
6858 |  | UINT16 | 2 | R | Canister monitoring state (Increase) | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
6859 |  | FLOAT | 4 | RW | Canister monitoring capacity (Increase) | [user defined unit], e.g. 50 kg.
6861 |  | FLOAT | 4 | R | Canister monitoring remaining capacity (Increase) | [user defined unit], e.g. 25 kg.
6863 |  | ASCII | 8 | R | Canister monitoring unit (Increase) | e.g. "kg"
6867 |  | UINT16 | 2 | R | Canister monitoring Decrease | 0 = Off 1 = On
6868 |  | UINT16 | 2 | R | Canister monitoring state Decrease | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
6869 |  | FLOAT | 4 | RW | Canister monitoring capacity Decrease | [user defined unit], e.g. 50 kg.
6871 |  | FLOAT | 4 | R | Canister monitoring remaining capacity Decrease | [user defined unit], e.g. 25 kg.
6873 |  | ASCII | 8 | R | Canister monitoring unit Decrease | e.g. "kg"
Controller 5 Parameter | [5 empty] | Only the available controllers are transferred in the data structure. Not all controllers are available for every measurement. In this case, the value "0" is returned in the cor responding registers.
7000 |  | UINT16 | 2 | R | Controller | 0 = Off 1 = On
7001 |  | UINT16 | 2 | R | Controller type | 1 = Proportional 2 = Single feedback control 3 = Compound loop 4 = Dosing contact
7002 |  | UINT16 | 2 | R | Control mode | Only with Compound loop 0 = Single feed forward 1 = Single feed backward 2 = Compound loop
7003 |  | UINT16 | 2 | RW | Operation mode | 0 = Automatic 1 = Manual
7004 |  | UINT16 | 2 | R | Adaption | Only with Single feedback control 1 = Dosing 0% 2 = Wait for X=20% 3 = Dosing 100% 4 = Measuring Dead Time 5 = Measuring Rise Time 6 = Dosing 0% 7 = Done 8 = Abort
7005 |  | UINT16 | 2 | R | Stop reason | 0 = - 1 = Stop / Sample water flow 2 = Stop: Extern stop / DI 3 = Stop: Positioner calibration 4 = Stop: Error measurment signal 5 = Stop / dosing error 6 = Stop: Missing Dosing unit 7 = Stop: Error flow signal 8 = Stop: External Input Error 9 = Stop: Input Ctrl. function 10 = Stop: Container empty 11 = Stop: Container error 12 = Stop: Lockout 13 = Stop: Calib. timeout 14 = Stop: Calibration active 15 = Stop: Boost Dosing 16 = Stop: Max. Dosing Timeout 17 = Stop: No flow 18 = Invalid setpoint
7006 |  | FLOAT | 4 | R | Dosing output | [%]
7008 |  | FLOAT | 4 | R | Controller output | [%]
7010 |  | FLOAT | 4 | R | act. setpoint | [user defined unit], only with Single feedback control, Compound loop and dosing contact
7012 |  | FLOAT | 4 | R | act. dosing factor | [%], only at Proportional control
7014 |  | FLOAT | 4 | RW | Manual dosing | [user defined unit], only in manual mode
7016 |  | UINT32 | 4 | RW | Feed delay time | [seconds]
7018 |  | UINT16 | 2 | R | Control direction | Only with Single feedback control and Compound loop control 0 = direct 1 = inverts
7019 |  | ASCII | 20 | R | Measuring Label | Label of the corresponding measurement
7029 |  | UINT16 | 2 | R | Controller status | 0 = Off 1 = Manual 2 = Automatic 3 = ECO mode 4 = Stopped 5 = hold
7030 |  | UINT16 | 2 | R | reserved
7031 |  | INT32 | 4 | R | reserved
7033 |  | INT32 | 4 | R | reserved
7035 |  | INT32 | 4 | R | reserved
7037 |  | INT32 | 4 | R | reserved
7039 |  | INT16 | 2 | R | reserved
7040 |  | FLOAT | 4 | RW | Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
7042 |  | FLOAT | 4 | RW | Xp | [%], only with Single feedback control
7044 |  | UINT32 | 4 | RW | Tn | [seconds], only with Single feedback control
7046 |  | FLOAT | 4 | RW | reserved
7048 |  | FLOAT | 4 | RW | Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
7050 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
7052 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
7054 |  | FLOAT | 4 | RW | reserved
7056 |  | UINT32 | 4 | RW | Tkonst | [seconds], only with Compound loop control
7058 |  | UINT32 | 4 | RW | Tvar | [seconds], only with Compound loop control
7060 |  | FLOAT | 4 | RW | Max.lin.correction | [%], only with Compound loop control
7062 |  | FLOAT | 4 | RW | Controller factor | Only with Compound loop control.
7064 |  | FLOAT | 4 | RW | Process agent factor | Only with Proportional control.
7066 |  | FLOAT | 4 | RW | Dosing factor | [%], only at Proportional control
7068 |  | FLOAT | 4 | RW | Zero threshold | [%], only with Compound loop control and Proportional control
7070 |  | UINT32 | 4 | RW | Ts | [seconds], only with adaptation
7072 |  | UINT32 | 4 | RW | Tu | [seconds], only with adaptation
7074 |  | INT32 | 4 | R | reserved
7076 |  | INT32 | 4 | R | reserved
7078 |  | INT32 | 4 | R | reserved
7080 |  | FLOAT | 4 | RW | ECO Xsh | [%], only with Single feedback control with actuator Pump 3P or Analog output 3P
7082 |  | FLOAT | 4 | RW | ECO Xp | [%], only with Single feedback control
7084 |  | UINT32 | 4 | RW | ECO Tn | [seconds], only with Single feedback control
7086 |  | FLOAT | 4 | RW | reserved
7088 |  | FLOAT | 4 | RW | ECO Setpoint | [user defined unit], only with Single feedback control, Compound loop control and dosing contact
7090 |  | FLOAT | 4 | RW | Max (2P) / Max Increase (3P) | Range 0 – 100
7092 |  | FLOAT | 4 | RW | Min (2P) / Max Decrease (3P) | Range 0 – 100
7094 |  | FLOAT | 4 | RW | reserved
7096 |  | UINT32 | 4 | RW | ECO Tkonst | [seconds], only with Compound loop control
7098 |  | UINT32 | 4 | RW | ECO Tvar | [seconds], only with Compound loop control
7100 |  | FLOAT | 4 | RW | ECO Max.lin.correction | [%], only with Compound loop control
7102 |  | FLOAT | 4 | RW | ECO Controller factor | Only with Compound loop control.
7104 |  | FLOAT | 4 | RW | ECO Process agent factor | Only with Proportional control.
7106 |  | FLOAT | 4 | RW | ECO Dosing factor | [%], only at Proportional control
7108 |  | FLOAT | 4 | RW | ECO Zero threshold | [%], only with Compound loop control and Proportional control
7110 |  | UINT32 | 4 | RW | ECO Ts | [seconds], only with adaptation
7112 |  | UINT32 | 4 | RW | ECO Tu | [seconds], only with adaptation
7114 |  | INT32 | 4 | R | reserved
7116 |  | INT32 | 4 | R | reserved
7118 |  | INT32 | 4 | R | reserved
7120 |  | UINT16 | 2 | R | Boost Dosing | 0 = Off 1 = On
7121 |  | UINT16 | 2 | R | Boost Dosing state | 0 = Inactive 1 = Active 2 = Delay controllers
7122 |  | FLOAT | 4 | RW | Boost Dosing Setpoint | [user defined unit]
7124 |  | UINT32 | 4 | RW | Boost Dosing Dosing duration | [seconds]
7126 |  | UINT16 | 2 | RW | Boost Dosing start | 1 = Boost Dosing started
7127 |  | UINT16 | 2 | RW | Boost Dosing stop | 1 = Boost Dosing stoped
7128 |  | UINT16 | 2 | R | Peak Dosing | 0 = Off 1 = On
7129 |  | UINT16 | 2 | R | Peak Dosing state | 0 = Inactive 1 = Raise 2 = Active 3 = Standby
7130 |  | FLOAT | 4 | RW | Peak Dosing Setpoint | [user defined unit]
7132 |  | UINT32 | 4 | RW | Peak Dosing Dosing duration | [seconds]
7134 |  | UINT16 | 2 | RW | Peak Dosing start | 1 = Peck Dosing started
7135 |  | UINT16 | 2 | RW | Peak Dosing stop | 1 = Peck Dosing stoped
Controller 5 Actuatur / Dosing
7300 |  | UINT16 | 2 | R | Actuator Type | 101 = Positioner w. Ym 102 = Positioner wo. Ym 103 = Pump 2P 104 = Dosing contact 105 = Analog output 2P 106 = Analog output 3P (single) 107 = Analog output 3P (dual) 108 = Pump 3P
7301 |  | UINT16 | 2 | R | Actuator Status (Increase) | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
7302 |  | UINT16 | 2 | R | Actuator Range (Increase) | Only with Analog output 2P and Analog output 3P (single) 0 = 0...20 1 = 4...20
7303 |  | UINT16 | 2 | R | Actuator Pump type (Increase) | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
7304 |  | UINT16 | 2 | R | Actuator max. Pulse/Min (Increase) | Only with Pump type Solenoid pump. e.g. 120
7305 |  | UINT32 | 4 | R | Actuator Tp (Increase) | [seconds], only with pump type dosing pump
7307 |  | UINT16 | 2 | R | Actuator Status Decrease | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
7308 |  | UINT16 | 2 | R | Actuator Range Decrease | [%], only with Analog output 3P (dual) 0 = 0...20 1 = 4...20
7309 |  | UINT16 | 2 | R | Actuator Pump type Decrease | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
7310 |  | UINT16 | 2 | R | Actuator max. Pulse/Min Decrease | Only with Pump type Solenoid pump. e.g. 120
7311 |  | UINT32 | 4 | R | Actuator Tp Decrease | [seconds], only with pump type dosing pump
7313 |  | UINT32 | 4 | R | Actuator Ty | [seconds.] ,only for positioner without Ym
7315 |  | FLOAT | 4 | R | Actuator Feedback Tolerance | [%], only for positioner with Ym
7317 |  | FLOAT | 4 | R | Actuator Feedback | [%], only for positioner with Ym
7319 |  | INT32 | 4 | R | reserved
7321 |  | INT32 | 4 | R | reserved
7323 |  | FLOAT | 4 | R | Consumption fo dosing agent (Increase) | [user defined unit], e.g. 91.6 l.
7325 |  | FLOAT | 4 | R | Current dosing (Increase) | [user defined unit], e.g. 0.5 l/h.
7327 |  | FLOAT | 4 | R | reserved
7329 |  | FLOAT | 4 | R | reserved
7331 |  | FLOAT | 4 | R | Average dosing of dosing agent (Increase) | [user defined unit], e.g. 10.3 l/h.
7333 |  | ASCII | 8 | R | Rate unit (Increase) | e.g. "l/h"
7337 |  | UINT16 | 2 | RW | reserved
7338 |  | FLOAT | 4 | R | Consumption fo dosing agent Decrease | [user defined unit], e.g. 91.6 l.
7340 |  | FLOAT | 4 | R | Current dosing Decrease | [user defined unit], e.g. 0.5 l/h.
7342 |  | FLOAT | 4 | R | reserved
7344 |  | FLOAT | 4 | R | reserved
7346 |  | FLOAT | 4 | R | Average dosing of dosing agent Decrease | [user defined unit], e.g. 10.3 l/h.
7348 |  | ASCII | 8 | R | Rate unit Decrease | e.g. "l/h"
7352 |  | UINT16 | 2 | RW | reserved
7353 |  | INT32 | 4 | R | reserved
7355 |  | INT32 | 4 | R | reserved
7357 |  | UINT16 | 2 | R | Canister monitoring (Increase) | 0 = Off 1 = On
7358 |  | UINT16 | 2 | R | Canister monitoring state (Increase) | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
7359 |  | FLOAT | 4 | RW | Canister monitoring capacity (Increase) | [user defined unit], e.g. 50 kg.
7361 |  | FLOAT | 4 | R | Canister monitoring remaining capacity (Increase) | [user defined unit], e.g. 25 kg.
7363 |  | ASCII | 8 | R | Canister monitoring unit (Increase) | e.g. "kg"
7367 |  | UINT16 | 2 | R | Canister monitoring Decrease | 0 = Off 1 = On
7368 |  | UINT16 | 2 | R | Canister monitoring state Decrease | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
7369 |  | FLOAT | 4 | RW | Canister monitoring capacity Decrease | [user defined unit], e.g. 50 kg.
7371 |  | FLOAT | 4 | R | Canister monitoring remaining capacity Decrease | [user defined unit], e.g. 25 kg.
7373 |  | ASCII | 8 | R | Canister monitoring unit Decrease | e.g. "kg"
Additional features Aquatics | [5 empty] | These additional features are only available in the Aquatics application.
10000 |  | UINT16 | 2 | R | Boost Dosing state | 0 = Inactive 1 = Active 2 = Delay controllers
10001 |  | FLOAT | 4 | RW | Boost Dosing Setpoint | [user defined unit]
10003 |  | UINT16 | 2 | RW | Boost Dosing start | 1 = Boost Dosing started
10004 |  | UINT16 | 2 | RW | Boost Dosing stop | 1 = Boost Dosing stoped
10005 |  | UINT16 | 2 | R | Peak Dosing state | 0 = Inactive 1 = Raise 2 = Active 3 = Standby
10006 |  | FLOAT | 4 | RW | Peak Dosing Setpoint | [user defined unit]
10008 |  | UINT16 | 2 | RW | Peak Dosing start | 1 = Peck Dosing started
10009 |  | UINT16 | 2 | RW | Peak Dosing stop | 1 = Peck Dosing stoped
10010 |  | UINT16 | 2 | R | ECO mode | 0 = Off 1 = On
10011 |  | UINT16 | 2 | RW | ECO Operation mode | 0 = Automatic 1 = ECO mode 2 = Normal mode
10012 |  | INT32 | 4 | R | reserved
10014 |  | INT32 | 4 | R | reserved
10016 |  | UINT16 | 2 | R | DIN | 0 = Off 1 = On
10017 |  | UINT16 | 2 | R | DIN Cl2 free | 0 = Off 1 = On
10018 |  | FLOAT | 4 | RW | DIN Cl2 free Limit value min | [user defined unit]
10020 |  | FLOAT | 4 | RW | DIN Cl2 free Limit value max | [user defined unit]
10022 |  | UINT16 | 2 | R | DIN pH | 0 = Off 1 = On
10023 |  | FLOAT | 4 | RW | DIN pH Limit value min | [user defined unit]
10025 |  | FLOAT | 4 | RW | DIN pH Limit value max | [user defined unit]
10027 |  | UINT16 | 2 | R | DIN ORP | 0 = Off 1 = On
10028 |  | FLOAT | 4 | RW | DIN ORP Limit value min | [user defined unit]
10030 |  | UINT16 | 2 | R | DIN Cl2 combined | 0 = Off 1 = On
10031 |  | FLOAT | 4 | RW | DIN Cl2 combined Limit calue max | [user defined unit]
10033 |  | UINT16 | 2 | R | DIN turbidity | 0 = Off 1 = On
10034 |  | FLOAT | 4 | RW | DIN turbidity Limit value max | [user defined unit]
10036 |  | INT32 | 4 | R | reserved
10038 |  | INT32 | 4 | R | reserved
10040 |  | UINT16 | 2 | R | Cedox mode | 0 = Off 1 = On
10041 |  | UINT16 | 2 | R | Cedox Operation mode | 0 = Not available 1 = Off 2 = Inactive By Normal Mode 3 = Stop: StartUp Delay
10042 |  | FLOAT | 4 | RW | Cedox Cl2 Setpoint min | [user defined unit]
10044 |  | FLOAT | 4 | RW | Cedox Cl2 Setpoint max | [user defined unit]
10046 |  | FLOAT | 4 | RW | Cedox ORP Setpoint | [user defined unit]
10048 |  | FLOAT | 4 | RW | Cedox ORP Setpoint ECO | [user defined unit]
10050 |  | INT32 | 4 | R | reserved
10052 |  | INT32 | 4 | R | reserved
10054 |  | UINT16 | 2 | R | Flocculation | 0 = Off 1 = On
10055 |  | UINT16 | 2 | R | Flocculation state | 0 = Off 1 = Active 2 = overdriven 3 = Stop: Timer 4 = Stopped: Flow 5 = Stop: pH 6 = Stop / Sample water flow 7 = Stop: Missing dosing unit 8 = Stop: Missing flow signal 9 = Stopped: Configuration Error 10 = Stop: Function
10056 |  | UINT16 | 2 | R | Flocculation Operation mode | 0 = Manual dosing rate 1 = Fixed flow rate
10057 |  | FLOAT | 4 | R | Flocculation current dosage value | [user defined unit]
10059 |  | UINT16 | 2 | R | Flocculation pH | 0 = Off 1 = On
10060 |  | FLOAT | 4 | RW | Flocculation pH Limit value min | [user defined unit]
10062 |  | FLOAT | 4 | RW | Flocculation pH Limit value max | [user defined unit]
10064 |  | INT32 | 4 | R | reserved
10066 |  | INT32 | 4 | R | reserved
10068 |  | UINT16 | 2 | R | Flocculation Actuator Type | 101 = Stellmotor mit Ym 102 = Stellmotor ohne Ym 103 = Pumpe 2P 104 = Dosierkontakt 105 = Stetig mA 2P 106 = Stetig mA 3P (single) 107 = Stetig mA 3P (dual) 108 = Pumpe 3P
10069 |  | UINT16 | 2 | R | Flocculation Actuator Status | 0 = Inactive 1 = Active
| 0 |  |  |  | Signal quality | 0 = Good 1 = Bad
| 1 |  |  |  | Hardware error 1 | Actuator: relay switching cycles exceeded.
| 2 |  |  |  | reserved
| 3 |  |  |  | Hardware error 3 | Mod 2RelFB: Hardware error
| 4 |  |  |  | reserved
| 5 |  |  |  | reserved
| 6 |  |  |  | reserved
| 7 |  |  |  | reserved
| 8 |  |  |  | Hardware error 8 | Relay switching cycles exceeded Actuator with feedback: input signal below the measurable range Mod 2AO: Load error
| 9 |  |  |  | Hardware error 9 | Actuator with feedback: Input signal above the measurable range
| 10 |  |  |  | Hardware error 10 | Hardware error
| 11 |  |  |  | Hardware error 11 | Factory calibration is missing
| 12 |  |  |  | reserved
| 13 |  |  |  | Hardware error 13 | Actuator in manual mode
| 14 |  |  |  | reserved
| 15 |  |  |  | reserved
10070 |  | UINT16 | 2 | R | Flocculation Actuator Range | Only with Analog output 2P and Analog output 3P (single) 0 = 0...20 1 = 4...20
10071 |  | UINT16 | 2 | R | Flocculation Actuator Pump type | Only with Pump 2P and Pump 3P. 0 = Solenoid pump 1 = Dosing pump
10072 |  | UINT16 | 2 | R | Flocculation Actuator max. Pulse/Min | Only with Pump type Solenoid pump. e.g. 120
10073 |  | UINT32 | 4 | R | Flocculation Actuator Tp | [seconds], only with pump type dosing pump
10075 |  | INT32 | 4 | R | reserved
10077 |  | INT32 | 4 | R | reserved
10079 |  | FLOAT | 4 | R | Flocculation Consumption fo dosing agent | [user defined unit], e.g. 91.6 l.
10081 |  | FLOAT | 4 | R | Flocculation Current dosing | [user defined unit], e.g. 0.5 l/h.
10083 |  | FLOAT | 4 | R | reserved
10085 |  | FLOAT | 4 | R | reserved
10087 |  | FLOAT | 4 | R | Flocculation Average dosing of dosing agent | [user defined unit], e.g. 10.3 l/h.
10089 |  | ASCII | 8 | RW | Flocculation Rate unit | e.g. "l/h"
10093 |  | UINT16 | 2 | R | reserved
10094 |  | INT32 | 4 | R | reserved
10096 |  | INT32 | 4 | R | reserved
10098 |  | UINT16 | 2 | R | Flocculation Canister monitoring | 0 = Off 1 = On
10099 |  | UINT16 | 2 | R | Flocculation Canister monitoring state | 0 = No selection 1 = Filled 2 = Minimum 3 = Empty 4 = Error
10100 |  | FLOAT | 4 | RW | Flocculation Canister monitoring capacity | [user defined unit], e.g. 50 kg.
10102 |  | FLOAT | 4 | R | Flocculation Canister monitoring remaining capacity | [user defined unit], e.g. 25 kg.
10104 |  | ASCII | 8 | R | Flocculation Canister monitoring unit | e.g. "kg"