## 700P_wt485
WT485 Reference List (700P)
Rivo I - III | [5 empty] | Ver.: V2.1.1
2026-05-21
Addr. | Bit | Type | No. of bytes | Access | Designation | Description
0 |  | ASCII | 12 | R | Software version | " Version:1.00 "
1 |  | ASCII | 28 | R | Module name | "Depolox Pool E700P"
2 |  | UINT16 | 2 | RW | Password of interface | 0...999
3 |  | ASCII | 12 | R | Module type | "E700P"
4 |  | UINT8 | 1 | R | Operation mode | not supported
5 |  | DS1 | 12 | R | Measured value Cl2 | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
6 |  | DS1 | 12 | R | Measured value pH | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
7 |  | DS1 | 12 | R | Measured value ORP | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
8 |  | DS1 | 12 | R | Measured value Cl-N | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
9 |  | DS1 | 12 | R | Measured value conductivity | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
10 |  | DS1 | 12 | R | Measured value temperature | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
11 |  | DS1 | 12 | R | Measured value positioner – feedback / Yout | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
12 |  | DS1 | 12 | R | Measured value controller output pH Yout | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
13 |  | DS1 | 12 | R | Measured value mA input 1 | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
14 |  | DS1 | 12 | R | Measured value mA input 2 | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
15 |  | FLOAT | 4 | RWP | Setpoint Cl2 | [user defined unit]
16 |  | INT16 | 2 | RWP | Xp Cl2 | [%]
17 |  | UINT16 | 2 | RWP | Tn Cl2 | [min], factor: 0.1
18 |  | FLOAT | 4 | RWP | Setpoint Cl2 (ECO) | [user defined unit]
19 |  | INT16 | 2 | RWP | Xp Cl2 (ECO) | [%]
20 |  | UINT16 | 2 | RWP | Tn Cl2 (ECO) | [min], factor: 0.1
21 |  | FLOAT | 4 | RWP | Setpoint pH | [pH]
22 |  | INT16 | 2 | RWP | Xp pH | [%]
23 |  | UINT16 | 2 | RWP | Tn pH | [min], factor: 0.1
24 |  | FLOAT | 4 | RWP | Setpoint Cedox | [user defined unit], setpoint ORP in CEDOX mode
25 |  | FLOAT | 4 | RWP | Setpoint Cedox (ECO) | [user defined unit]. setpoint ORP in CEDOX mode (ECO)
26 |  | FLOAT | 4 | RWP | Cedox chlorine setpoint | not supported
27 |  | FLOAT | 4 | RWP | Cedox chlorine setpoint limit min | [user defined unit]
28 |  | FLOAT | 4 | RWP | Cedox chlorine setpoint limit max | [user defined unit]
29 |  | FLOAT | 4 | RWP | Setpoint total chlorine | [user defined unit]
30 |  | INT16 | 2 | RWP | Xp total chlorine | [%]
31 |  | UINT16 | 2 | RWP | Tn total chlorine | [min], factor: 0.1
32 |  | FLOAT | 4 | RWP | Setpoint conductivity | [user defined unit]
33 |  | INT16 | 2 | RWP | Xp conductivity | [%]
34 |  | UINT16 | 2 | RWP | Tn conductivity | [min], factor: 0.1
35 |  | FLOAT | 4 | RWP | Limit value Cl2 min 1 | [user defined unit]
36 |  | FLOAT | 4 | RWP | Limit value Cl2 max 1 | [user defined unit]
37 |  | FLOAT | 4 | RWP | Limit value Cl2 hysteresis 1 | [user defined unit]
38 |  | FLOAT | 4 | RWP | Limit value Cl2 min 2 | [user defined unit]
39 |  | FLOAT | 4 | RWP | Limit value Cl2 max 2 | [user defined unit]
40 |  | FLOAT | 4 | RWP | Limit value Cl2 hysteresis 2 | [user defined unit]
41 |  | FLOAT | 4 | RWP | Limit value pH min 1 | [pH]
42 |  | FLOAT | 4 | RWP | Limit value pH max 1 | [pH]
43 |  | FLOAT | 4 | RWP | Limit value pH hysteresis 1 | [pH]
44 |  | FLOAT | 4 | RWP | Limit value pH min 2 | [pH]
45 |  | FLOAT | 4 | RWP | Limit value pH max 2 | [pH]
46 |  | FLOAT | 4 | RWP | Limit value pH hysteresis 2 | [pH]
47 |  | FLOAT | 4 | RWP | Limit value ORP min 1 | [mV]
48 |  | FLOAT | 4 | RWP | Limit value ORP max 1 | [mV]
49 |  | FLOAT | 4 | RWP | Limit value hysteresis 1 | [mV]
50 |  | FLOAT | 4 | RWP | Limit value ORP min 2 | [mV]
51 |  | FLOAT | 4 | RWP | Limit value ORP max 2 | [mV]
52 |  | FLOAT | 4 | RWP | Limit value ORP hysteresis 2 | [mV]
53 |  | FLOAT | 4 | RWP | Limit value total chlorine min 1 | [user defined unit]
54 |  | FLOAT | 4 | RWP | Limit value total chlorine max 1 | [user defined unit]
55 |  | FLOAT | 4 | RWP | Limit value total chlorine hysteresis 1 | [user defined unit]
56 |  | FLOAT | 4 | RWP | Limit value total chlorine min 2 | [user defined unit]
57 |  | FLOAT | 4 | RWP | Limit value total chlorine max 2 | [user defined unit]
58 |  | FLOAT | 4 | RWP | Limit value total chlorine hysteresis 2 | [user defined unit]
59 |  | FLOAT | 4 | RWP | Limit value conductivity min 1 | [user defined unit]
60 |  | FLOAT | 4 | RWP | Limit value conductivity max 1 | [user defined unit]
61 |  | FLOAT | 4 | RWP | Limit value conductivity hysteresis 1 | [user defined unit]
62 |  | FLOAT | 4 | RWP | Limit value conductivity min 2 | [user defined unit]
63 |  | FLOAT | 4 | RWP | Limit value conductivity max 2 | [user defined unit]
64 |  | FLOAT | 4 | RWP | Limit value conductivity hysteresis 2 | [user defined unit]
65 |  | UINT8 | 1 | R | Relay outputs 1
| 0 |  |  |  |  | 0x01 – K1
| 1 |  |  |  |  | 0x02 – K2
| 2 |  |  |  |  | 0x04 – K3
| 3 |  |  |  |  | 0x08 – K4
| 4 |  |  |  |  | 0x10 – K5
| 5 |  |  |  |  | 0x20 – K6
| 6 |  |  |  |  | 0x40 – K7
| 7 |  |  |  |  | 0x80 – K8
66 |  | UINT8 | 1 | R | Relay outputs 2
| 0 | UINT8 |  |  |  | 0x01 – K21
| 1 | UINT8 |  |  |  | 0x02 – K22
| 2 | UINT8 |  |  |  | 0x04 – K23
| 3 | UINT8 |  |  |  | 0x04 – K24
| 4 | UINT8 |  |  |  | reserved
| 5 | UINT8 |  |  |  | reserved
| 6 | UINT8 |  |  |  | reserved
| 7 | UINT8 |  |  |  | reserved
67 |  | UINT8 | 1 | R | Digital inputs
| 0 |  |  |  |  | 0x01 – Digital input 1
| 1 |  |  |  |  | 0x02 – Digital input 2
| 2 |  |  |  |  | 0x04 – Digital input 3
| 3 |  |  |  |  | 0x08 – Sample water stop
| 4 |  |  |  |  | reserved
| 5 |  |  |  |  | reserved
| 6 |  |  |  |  | reserved
| 7 |  |  |  |  | reserved
68 |  | UINT32 | 4 | R | Error code | not supported
69 |  | ASCII | 20 | RWP | System name | e.g. "DEPOLOX Pool E 700 P"
70 |  | ASCII | 10 | RWP | Date | not supported
71 |  | ASCII | 5 | RWP | Time | not supported
72 |  | INT16 | 2 | R | Limit contact messages
| 0 |  |  |  |  | 0x0001 – Limit contact 1
| 1 |  |  |  |  | 0x0002 – Limit contact 2
| 2 |  |  |  |  | 0x0004 – Limit contact 3
| 3 |  |  |  |  | 0x0008 – Limit contact 4
| 4 |  |  |  |  | 0x0010 – Limit contact 5
| 5 |  |  |  |  | 0x0020 – Limit contact 6
| 6 |  |  |  |  | 0x0040 – Limit contact 7
| 7 |  |  |  |  | 0x0080 – Limit contact 8
73 |  | FLOAT | 4 | R | Act. setpoint chlorine | [user defined unit]
74 |  | FLOAT | 4 | R | Act. dosing rate/control rate chlorine Yout | [%]
75 |  | FLOAT | 4 | R | Act. setpoint pH | [pH]
76 |  | FLOAT | 4 | R | Act. dosing rate/control rate pH Yout | [%]
77 |  | FLOAT | 4 | R | Act. setpoint total chlorine | [user defined unit]
78 |  | FLOAT | 4 | R | Act. dosing rate/control value total chlorine Yout | [%]
79 |  | FLOAT | 4 | R | Act. setpoint conductivity | [user defined unit]
80 |  | FLOAT | 4 | R | Act. dosing rate/control value conductivity Yout | [%]
81 |  | FLOAT | 4 | RWP | DIN limit value chlorine MIN | [user defined unit]
82 |  | FLOAT | 4 | RWP | DIN limit value chlorine MAX | [user defined unit]
83 |  | FLOAT | 4 | RWP | DIN limit value chlorine hysteresis | [user defined unit]
84 |  | FLOAT | 4 | RWP | DIN limit value pH MIN | [pH]
85 |  | FLOAT | 4 | RWP | DIN limit value pH MAX | [pH]
86 |  | FLOAT | 4 | RWP | DIN limit value pH hysteresis | [pH]
87 |  | FLOAT | 4 | RWP | DIN limit value ORP MIN | [mV]
88 |  | FLOAT | 4 | RWP | DIN limit value ORP hysteresis | [mV]
89 |  | FLOAT | 4 | RWP | DIN limit value total chlorine MAX | [user defined unit]
90 |  | FLOAT | 4 | RWP | DIN limit value total Hysteresis | [user defined unit]