## DepoloxPool_wt485
WT485 Reference List (DepoloxPool)
Rivo I - III | [5 empty] | Ver.: V2.1.1
2026-05-21
Addr. | Bit | Type | No. of bytes | Access | Designation | Description
0 |  | ASCII | 12 | R | Date of the software version | " V: 0A.02 "
1 |  | ASCII | 28 | R | Module name | "POOL-Manager DEPOLOX POOL21"
2 |  | UINT16 | 2 | RW | Password of the interface | 0...999
3 |  | ASCII | 12 | R | Module type | "Depolox Pool"
4 |  | UINT8 | 1 | R | Mode | not supported
5 |  | DS1 | 12 | R | Measured value Cl2 | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
6 |  | DS1 | 12 | R | Measured value pH | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
7 |  | DS1 | 12 | R | Measured value ORP | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
8 |  | DS1 | 12 | R | Measured value Cl-N | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
9 |  | DS1 | 12 | R | Measured value conductivity | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
10 |  | DS1 | 12 | R | Measured value temperature | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
11 |  | DS1 | 12 | R | Measured value positioner – feedback / Yout | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
12 |  | DS1 | 12 | R | Measured value controller output pH Yout | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
13 |  | UINT8 | 1 | R | Dosing output, alarms, release (DIN-Fct) | not supported
14 |  | UINT8 | 1 | R | Digital inputs
| 0 |  |  |  |  | 0x01 – Digital input 1 (Sample water stop)
| 1 |  |  |  |  | 0x02 – Digital input 2
| 2 |  |  |  |  | 0x04 – Digital input 3
| 3 |  |  |  |  | 0x04 – Digital input 4
| 4 |  |  |  |  | reserved
| 5 |  |  |  |  | reserved
| 6 |  |  |  |  | reserved
| 7 |  |  |  |  | reserved
15 |  | UINT16 | 2 | R | Error status | not supported
16 |  | INT16 | 2 | R | Current setpoint Wi Cl2 | Current setpoint Cl2 1, [user defined unit], factor: 0.01
17 |  | INT16 | 2 | RWP | Setpoint Wi Cl2(1) | Setpoint Cl2 1, [user defined unit], factor: 0.01
18 |  | INT16 | 2 | RWP | Xp Cl2 | [%]
19 |  | UINT16 | 2 | RWP | Tn Cl2 | [min], factor: 0.1
20 |  | INT16 | 2 | RWP | Setpoint Wi Cl2(ECO) | Setpoint Cl2 2 (ECO mode), [user defined unit], factor: 0.01
21 |  | INT16 | 2 | RWP | Xp Cl2(ECO) | [%]
22 |  | UINT16 | 2 | RWP | Tn Cl2(ECO) | [min], factor: 0.1
23 |  | INT16 | 2 | RWP | Setpoint Wi pH | factor: 0.01
24 |  | INT16 | 2 | RWP | Xp pH | [%]
25 |  | UINT16 | 2 | RWP | Tn pH | [min], factor: 0.1
26 |  | INT16 | 2 | RWP | Setpoint Conductivity | [user defined unit], factor: 0.1
27 |  | INT16 | 2 | RWP | Xp Conductivity | [%]
28 |  | INT16 | 2 | RWP | Setpoint Cl-N | [user defined unit], factor: 0.01
29 |  | INT16 | 2 | RWP | Limit Cl2 min | [user defined unit], factor: 0.01
30 |  | INT16 | 2 | RWP | Limit Cl2 max | [user defined unit], factor: 0.01
31 |  | INT16 | 2 | RWP | Limit pH min | [pH], factor: 0.01
32 |  | INT16 | 2 | RWP | Limit pH max | [pH], factor: 0.01
33 |  | INT16 | 2 | RWP | Limit ORP min | [mV]
34 |  | INT16 | 2 | RWP | Limit ORP max | [mV]
35 |  | INT16 | 2 | RWP | Limit Cl-N min | [user defined unit], factor: 0.01
36 |  | INT16 | 2 | RWP | Limit Cl-N max | [user defined unit], factor: 0.01
37 |  | INT16 | 2 | RWP | Limit conductivity min | [user defined unit], factor: 0.1
38 |  | INT16 | 2 | RWP | Limit conductivity max | [user defined unit], factor: 0.1
39 |  | ASCII | 7 | RWP | Date | not supported
40 |  | INT16 | 2 | RWP | Chlorine limit hysteresis | [user defined unit], factor: 0.01
41 |  | INT16 | 2 | RWP | pH limit hysteresis | [pH], factor: 0.01
42 |  | INT16 | 2 | RWP | ORP limit hysteresis | [mV]
43 |  | INT16 | 2 | RWP | Cl-N limit hysteresis | [user defined unit], factor: 0.01
44 |  | INT16 | 2 | RWP | Conductivity limit hysteresis | [user defined unit], factor: 0.1
45 |  | UINT16 | 2 | RWP | Ty Cl2 | [sec]
46 |  | UINT16 | 2 | RWP | Tp Cl2 | [sec]
47 |  | INT16 | 2 | RWP | Ymin Cl2 | [%], factor: 0.1
48 |  | INT16 | 2 | RWP | Ymax Cl2 | [%], factor: 0.1
49 |  | UINT16 | 2 | RWP | Tu Cl2 | [sec]
50 |  | UINT16 | 2 | RWP | Ts Cl2 | [sec]
51 |  | UINT16 | 2 | RWP | Ty pH | [sec]
52 |  | UINT16 | 2 | RWP | Tp pH | [sec]
53 |  | INT16 | 2 | RWP | Xsh pH | [%], factor: 0.1
54 |  | INT16 | 2 | RWP | Ymin pH | [%], factor: 0.1
55 |  | INT16 | 2 | RWP | Ymax pH | [%], factor: 0.1
56 |  | UINT16 | 2 | RWP | Tp conductivity | [sec]
57 |  | INT16 | 2 | RWP | Ymin conductivity | [%], factor: 0.1
58 |  | INT16 | 2 | RWP | Ymax conductivity | [%], factor: 0.1
59 |  | UINT16 | 2 | RWP | CL-N On time | not supported
60 |  | UINT16 | 2 | RWP | CL-N Off time | not supported
61 |  | INT16 | 2 | RWP | Flocculation circulation | [user defined unit]
62 |  | INT16 | 2 | RWP | Flocculation dosing rate of the pump | not supported
63 |  | INT16 | 2 | RWP | Flocculation concentration | [user defined unit], factor: 0.1
64 |  | INT16 | 2 | RWP | Flocculation dosing rate | [%]
65 |  | INT16 | 2 | RWP | Flocculation dosing rate (ECO) | not supported
66 |  | INT16 | 2 | RWP | Flocculation pH min value | [pH], factor: 0.01
67 |  | INT16 | 2 | RWP | Flocculation pH max value | [pH], factor: 0.01
68 |  | INT16 | 2 | RWP | Measuring range Cl2 | not supported
69 |  | INT16 | 2 | RWP | Measuring range Cl-N | not supported
70 |  | UINT8 | 1 | RWP | Measuring range pH zero | not supported
71 |  | UINT8 | 1 | RWP | Measuring range pH end value | not supported
72 |  | UINT8 | 1 | RWP | Measuring range ORP zero | not supported
73 |  | UINT8 | 1 | RWP | Measuring range ORP end value | not supported
74 |  | UINT8 | 1 | RWP | Measuring range Conductivity | not supported
75 |  | UINT16 | 2 | RWP | Selection positioner Cl2 | not supported
76 |  | UINT8 | 1 | RWP | Max. pulses for the solenoid metering pump Cl2 | not supported
77 |  | UINT8 | 1 | R | Application | not supported
78 |  | UINT16 | 2 | RWP | Selection positioner pH | not supported
79 |  | UINT8 | 1 | RWP | Control direction pH | not supported
80 |  | UINT8 | 1 | RWP | Max. pulses for pulse pump pH | not supported
81 |  | UINT16 | 2 | RWP | Selection positioner conductivity | not supported
82 |  | UINT8 | 1 | RWP | Max. pulses for pulse pump conductivity | not supported
83 |  | UINT8 | 1 | RWP | Language | not supported
84 |  | UINT8 | 1 | RWP | Measured value filter | not supported
85 |  | UINT8 | 1 | RWP | Hold function | not supported
86 |  | UINT8 | 1 | RWP | RS232 – interface | not supported
87 |  | UINT8 | 1 | RWP | Flocculation | not supported
88 |  | UINT8 | 1 | RWP | DIN function | not supported
89 |  | UINT8 | 1 | RWP | CL-N mode | not supported
90 |  | UINT16 | 2 | RWP | Line diagram 1 | not supported
91 |  | UINT16 | 2 | RWP | Line diagram 2 | not supported
92 |  | UINT16 | 2 | RWP | Line diagram 3 | not supported
93 |  | UINT16 | 2 | RWP | Line diagram 4 | not supported
94 |  | UINT8 | 1 | RWP | Analogue output signal | not supported
95 |  | UINT8 | 1 | RWP | Analogue output 1 assignment | not supported
96 |  | UINT8 | 1 | RWP | Analogue output 2 assignment | not supported
97 |  | UINT8 | 1 | RWP | Analogue output 3 assignment | not supported
98 |  | UINT8 | 1 | RWP | Analogue output 4 assignment | not supported
99 |  | UINT8 | 1 | RWP | Alarm 1 function | not supported
100 |  | UINT8 | 1 | RWP | Alarm 2 function | not supported
101 |  | UINT8 | 1 | RWP | Alarm 3 function | not supported
102 |  | UINT8 | 1 | RWP | Alarm 4 function | not supported
103 |  | UINT16 | 2 | RWP | Alarm 1 assignment | not supported
104 |  | UINT16 | 2 | RWP | Alarm 2 assignment | not supported
105 |  | UINT16 | 2 | RWP | Alarm 3 assignment | not supported
106 |  | UINT16 | 2 | RWP | Alarm 4 assignment | not supported
107 |  | UINT16 | 2 | RWP | Alarm 1 delay time | [sec]
108 |  | UINT16 | 2 | RWP | Alarm 2 delay time | [sec]
109 |  | UINT16 | 2 | RWP | Alarm 3 delay time | [sec]
110 |  | UINT16 | 2 | RWP | Alarm 4 delay time | [sec]
111 |  | UINT16 | 2 | RWP | Dosing delay time | [sec]
112 |  | UINT16 | 2 | RWP | Max. dosing time | [sec]
113 |  | UINT16 | 2 | RWP | Sample water delay time | not supported
114 |  | UINT16 | 2 | RWP | Digital input 2 assignment | not supported
115 |  | UINT16 | 2 | RWP | Digital input 3 assignment | not supported
116 |  | ASCII | 12 | RWP | System name | -
117 |  | UINT32 | 4 | R | Error | not supported
118 |  | UINT8 | 1 | R | Relay
| 0 |  |  |  |  | 0x01 – K1
| 1 |  |  |  |  | 0x02 – K2
| 2 |  |  |  |  | 0x04 – K3
| 3 |  |  |  |  | 0x08 – K4
| 4 |  |  |  |  | 0x10 – K5
| 5 |  |  |  |  | 0x20 – K6
| 6 |  |  |  |  | 0x40 – K7
| 7 |  |  |  |  | 0x80 – K8
119 |  | FLOAT | 4 | R | Cl2 cell current | -
120 |  | FLOAT | 4 | R | pH cell voltage | -
121 |  | FLOAT | 4 | R | ORP cell voltage | -
122 |  | FLOAT | 4 | R | Cl-N cell current | -
123 |  | FLOAT | 4 | R | Conductivity cell current | not supported
124 |  | FLOAT | 4 | R | Conductivity cell voltage | not supported
125 |  | FLOAT | 4 | R | Conductivity NaCl | not supported
126 |  | FLOAT | 4 | R | Conductivity NaCl in % | not supported
127 |  | FLOAT | 4 | R | Temperature in digits | not supported
128 |  | FLOAT | 4 | R | Positioner feedback in digits | not supported
129 |  | UINT8 | 1 | RWP | Calibration data index | not supported
130 |  | ASCII | 33 | R | Calibration data chlorine | not supported
131 |  | ASCII | 33 | R | Calibration data pH | not supported
132 |  | ASCII | 33 | R | Calibration data ORP | not supported
133 |  | ASCII | 33 | R | Calibration data Cl-N | not supported
134 |  | ASCII | 33 | R | Calibration data conductivity | not supported
135 |  | FLOAT | 4 | R | Dosing average chlorine | -
136 |  | FLOAT | 4 | R | Dosing average pH | -
137 |  | FLOAT | 4 | R | Dosing average conductivity | -
138 |  | FLOAT | 4 | R | Dosing average flocculation | -
139 |  | FLOAT | 4 | R | Conductivity TDS display | not supported
140 |  | INT16 | 2 | RWP | Conductivity TDS factor | not supported
141 |  | UINT8 | 1 | RWP | Additional selection for conductivity | not supported
142 |  | UINT8 | 1 | RWP | Conductivity reference temperature | not supported
143 |  | UINT8 | 1 | R | - | not supported
144 |  | UINT8 | 1 | RWP | Controller mode | not supported
145 |  | UINT8 | 1 | RWP | Dynamic ECO signal (mA input) | not supported
146 |  | UINT8 | 1 | RWP | Alarms / controller at peak chlorination | not supported
147 |  | INT16 | 2 | RWP | Setpoint hysteresis at dosing contact | [user defined unit], factor: 0.01
148 |  | INT16 | 2 | RWP | Min. setpoint at CEDOX | [user defined unit], factor: 0.01
149 |  | INT16 | 2 | RWP | Max. setpoint at CEDOX | [user defined unit], factor: 0.01
150 |  | UINT16 | 2 | RWP | Tu Cl2 ECO | [sec]
151 |  | UINT16 | 2 | RWP | Ts Cl2 ECO | [sec]
152 |  | INT16 | 2 | RWP | Setpoint ORP at CEDOX | [mV]
153 |  | INT16 | 2 | RWP | Setpoint ORP ECO at CEDOX | [mV]
154 |  | INT16 | 2 | RWP | Hysteresis at CEDOX | not supported
155 |  | UINT16 | 2 | RWP | CEDOX time | [min]
156 |  | INT16 | 2 | RWP | Upot | [mV]
157 |  | INT16 | 2 | RWP | CAN-Bus Segment Address | not supported
158 |  | INT16 | 2 | RWP | RS485-Bus Address | not supported
159 |  | INT16 | 2 | RWP | Circulation capacity | not supported
160 |  | INT16 | 2 | RWP | Circulation capacity ECO | not supported
161 |  | INT16 | 2 | RWP | Circulation capacity ECO on | not supported
162 |  | UINT16 | 2 | RWP | Min. switch-on time at dosing contact | [min]
163 |  | INT16 | 2 | RWP | Peak chlorination setpoint | [user defined unit], factor: 0.01
164 |  | UINT16 | 2 | RWP | Duration of peak chlorination | not supported
165 |  | UINT16 | 2 | RWP | Max. delay until peak peak chlorination setpoint is reached | not supported
166 |  | UINT8 | 1 | RWP | Peak chlorination interval | not supported
167 |  | ASCII | 8 | R | Peak chlorination switch-on time 1 | not supported
168 |  | ASCII | 8 | R | Peak chlorination switch-on time 2 | not supported
169 |  | ASCII | 8 | R | Peak chlorination switch-on time 3 | not supported
170 |  | ASCII | 8 | R | Peak chlorination switch-on time 4 | not supported
171 |  | ASCII | 8 | R | Peak chlorination switch-on time 5 | not supported
172 |  | UINT8 | 1 | W | Reading index for line diagram 1 | not supported
173 |  | UINT8 | 1 | W | Reading index for line diagram 2 | not supported
174 |  | UINT8 | 1 | W | Reading index for line diagram 3 | not supported
175 |  | UINT8 | 1 | W | Reading index for line diagram 4 | not supported
176 |  | ASCII | 240 | R | Line diagram data selected by reading index | not supported
177 |  | ASCII | 15 | R | Version Main-Software | -