## PCSplus(1)_wt485
WT485 Reference List (PCSplus(1))
Rivo I - III | [5 empty] | Ver.: V2.1.1
2026-05-21
Addr. | Bit | Type | No. of bytes | Access | Designation | Description
0 |  | ASCII | 12 | R | Date of the software version | " V: 0A.02 "
1 |  | ASCII | 28 | R | Module name | "COMMON Electronic - PCS plus"
2 |  | UINT16 | 2 | RW | Password of the interface | 0...999
3 |  | ASCII | 12 | R | Module type | e.g. PCS+R
4 |  | UINT8 | 1 | R | Mode | not supported
5 |  | DS1 | 12 | R | Measured value Cl2 | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
6 |  | DS1 | 12 | R | Measured value pH | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
7 |  | DS1 | 12 | R | Measured value ORP | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
8 |  | DS1 | 12 | R | Measured value temperature | Data structure 1
|  | INT16 | 2 |  | Value
|  | INT16 | 2 |  | Range start
|  | INT16 | 2 |  | Range end
|  | ASCII | 5 |  | Unit
|  | INT8 | 1 |  | Divider
9 |  | INT16 | 2 | RWP | Limit Cl2 min | [user defined unit], factor: 0.01
10 |  | INT16 | 2 | RWP | Limit Cl2 max | [user defined unit], factor: 0.01
11 |  | INT16 | 2 | RWP | Limit pH min | [pH], factor: 0.01
12 |  | INT16 | 2 | RWP | Limit pH max | [pH], factor: 0.01
13 |  | INT16 | 2 | RWP | Limit ORP min | [mV]
14 |  | INT16 | 2 | RWP | Limit ORP max | [mV]
15 |  | INT16 | 2 | RWP | Limit Temp min | [user defined unit], factor: 0.01
16 |  | INT16 | 2 | RWP | Limit Temp max | [user defined unit], factor: 0.01
17 |  | UINT16 | 2 | RWP | Alarm 1 assignment | not supported
18 |  | UINT8 | 1 | RWP | Alarm 1 function | not supported
19 |  | UINT16 | 2 | RWP | Alarm 1 delay time | [sec]
20 |  | UINT16 | 2 | RWP | Alarm 2 assignment | not supported
21 |  | UINT8 | 1 | RWP | Alarm 2 function | not supported
22 |  | UINT16 | 2 | RWP | Alarm 2 delay time | [sec]
23 |  | UINT8 | 1 | RWP | Language | not supported
24 |  | UINT8 | 1 | RWP | Hold function | not supported
25 |  | UINT8 | 1 | RWP | Menu short/long | not supported
26 |  | UINT8 | 1 | RWP | Standby | not supported
27 |  | ASCII | 6 | RWP | Date | not supported
28 |  | UINT16 | 2 | RWP | Sample water delay time | not supported
29 |  | UINT16 | 2 | RWP | Dosing delay time | [min]
30 |  | UINT16 | 2 | RWP | Max. dosing time | not supported
31 |  | UINT8 | 1 | RWP | Analogue output signal | not supported
32 |  | UINT8 | 1 | RWP | Analogue output 1 assignment | not supported
33 |  | UINT8 | 1 | RWP | Analogue output 2 assignment | not supported
34 |  | UINT8 | 1 | RWP | Analogue output 3 assignment | not supported
35 |  | UINT8 | 1 | RWP | Analog output range Cl2 | not supported
36 |  | ASCII | 16 | R | Software Number | not supported
37 |  | ASCII | 16 | R | Software Version | -
38 |  | ASCII | 16 | R | Software Date | not supported
39 |  | UINT16 | 2 | R | Sensor selection | not supported
40 |  | UINT16 | 2 | R | Display selecton | not supported
41 |  | UINT32 | 4 | R | Error | not supported
42 |  | INT16 | 2 | RWP | Setpoint Wi Cl2 | Setpoint Cl2, [user defined unit], factor: 0.01
43 |  | INT16 | 2 | RWP | Xp Cl2 | [%]
44 |  | UINT16 | 2 | RWP | Tn Cl2 | [min], factor: 0.1
45 |  | UINT8 | 1 | RWP | Selection positioner Cl2 | not supported
46 |  | UINT16 | 2 | RWP | Ty Cl2 | [sec]
47 |  | INT16 | 2 | RWP | Max. pulses for pulse pump Cl2 | not supported
48 |  | INT16 | 2 | RWP | Tp Cl2 | [sec]
49 |  | UINT16 | 2 | RWP | Dose contact Min. On Time Cl2 | [min], factor: 0.1
50 |  | INT16 | 2 | RWP | Dose contact Hysteresis Cl2 | [user defined unit], factor: 0.01
51 |  | UINT16 | 2 | RWP | Tu Cl2 | [sec]
52 |  | UINT16 | 2 | RWP | Ts Cl2 | [min], factor: 0.1
53 |  | INT16 | 2 | R | Act. dosing rate/control rate Cl2 | [%]
54 |  | INT16 | 2 | RWP | Setpoint Wi pH | factor: 0.01
55 |  | INT16 | 2 | RWP | Xp pH | [%]
56 |  | UINT16 | 2 | RWP | Tn pH | [min], factor: 0.1
57 |  | UINT8 | 1 | RWP | Selection positioner pH | not supported
58 |  | UINT16 | 2 | RWP | Ty pH | [sec]
59 |  | INT16 | 2 | RWP | Max. pulses for pulse pump pH | not supported
60 |  | INT16 | 2 | RWP | Tp pH | [sec]
61 |  | INT16 | 2 | RWP | Hysteresis | not supported
62 |  | UINT8 | 1 | RWP | Controller direction | not supported
63 |  | INT16 | 2 | R | Act. dosing rate/control rate pH | [%]
64 |  | INT16 | 2 | RWP | Setpoint Wi Cl2(2)/Cl-N | not supported
65 |  | INT16 | 2 | RWP | Xp Cl2(2)/Cl-N | not supported
66 |  | INT16 | 2 | RWP | Tn Cl2(2)/Cl-N | not supported
67 |  | UINT8 | 1 | RWP | Selection positioner Cl2(2)/Cl-N | not supported
68 |  | INT16 | 2 | RWP | Max. pulses for pulse pump Cl2(2)/Cl-N | not supported
69 |  | INT16 | 2 | RWP | Tp Cl2(2)/Cl-N | not supported
70 |  | INT16 | 2 | RWP | Dose contact Min. On Time Cl2(2)/Cl-N | not supported
71 |  | INT16 | 2 | RWP | Dose contact Min. Off Time Cl2(2)/Cl-N | not supported
72 |  | INT16 | 2 | RWP | Dose contact Hysteresis Cl2(2)/Cl-N | not supported
73 |  | UINT16 | 2 | RWP | Tu Cl2(2)/Cl-N | not supported
74 |  | UINT16 | 2 | RWP | Ts Cl2(2)/Cl-N | not supported
75 |  | INT16 | 2 | R | Act. dosing rate/control rate Cl2(2)/Cl-N | not supported
76 |  | INT16 | 2 | RWP | man. temperature compensation | not supported
77 |  | UINT16 | 2 | R | State Digitalinputs | not supported
78 |  | INT16 | 2 | R | Cell current Cl2 | not supported
79 |  | INT16 | 2 | R | Cell voltage pH | not supported
80 |  | INT16 | 2 | R | Cell current / cell voltage mV/Cl2(2)/Cl-N | not supported
81 |  | INT16 | 2 | RWP | Dosing time at manual mode | not supported
82 |  | ASCII | 16 | R | Calibration values Cl2 | not supported
83 |  | ASCII | 16 | R | Calibration date Cl2 | not supported
84 |  | ASCII | 16 | R | Calibration values pH | not supported
85 |  | ASCII | 16 | R | Calibration date pH | not supported
86 |  | ASCII | 16 | R | Calibration values mV/Cl2(2)/Cl-N | not supported
87 |  | ASCII | 16 | R | Calibration date mV/Cl2(2)/Cl-N | not supported
88 |  | ASCII | 16 | R | Calibration values temperature | not supported
89 |  | ASCII | 16 | R | Calibration date temperature | not supported